## INFO
CALCULATION SHEET SMART READINESS INDICATOR FOR BUILDINGS
Calculation sheet for SRI assessment method A/B
Version 4.5
This file contains a calculation model for the SRI. The calculation method is based on the outcomes of the second technical study on the smart ready indicator, as described in chapter 1 of the technical study report (doi: 10.2833/41100) and the EC delegated act. Some of the elements comprising the calculation method (services, functionality, weightings, impact scores, etc.) can be altered. This spreadsheet is meant as a tool to support the SRI testing and implementation phase in EU Member States. Using this tool can by no means lead to any claims on an actual score or certificate for a building.
Using this tool is subject to terms and conditions (see tab: terms and conditions). By using this tool, you confirm to comply to these.
Legal Notice This document has been prepared for the European Commission however it reflects the views only of the authors, and the Commission cannot be held responsible for any use which may be made of the information contained therein.
E-mail: support@smartreadinessindicator.eu
Usage
This spreadsheet contains the calculation methodology for assessing the SRI of a building. It contains the following tabs:
* Building Information | Mandatory: Choose your preferred language as a first step, and use this sheet to provide general information on the building and its technical building systems, meanwhile indicate your assessment method A or B, and to indicate whether a domain is present/absent in your assessment
* Calculation | Mandatory: Use this sheet to indicate whether a service is appliable in your assessment, and to indicate the functionality level for each service.
* Results | Informative: Use this sheet to check the final calculation results
* Weightings | Informative: Use only if you wish to provide user-defined weighting factors
* overview_of_services | Informative: This is the list with all smart ready services and their functionality levels. (IMPORTANT) Mandatory to use this sheet to enable/disable services manually. Mandatory when adding extra services, 45 extra services (5 per domain) have been already placed in the list, indicate the functionality levels for each of your added services.
* tabs for each domain: H, DHW, C, V, L, DE, E, EV, MC | Informative: These tabs provide further details on the various services, including the provisional impact scores for each of the service levels; (IMPORTANT) Mandatory when adding extra services, add the impact scores for each of the functionality levels of your added services
Instructions
Input fields: use these yellow input fields to provide the requested information (see below)
All other fields: all other fields are filled automatically and cannot be edited
List of abbreviations
BACS | Building Automation and Control System
CHP | Combined Heat and Power
CW | Cold Water
DHW | Domestic Hot Water
DR | Demand Response
DSM | Demand Side Management
EV | Electric Vehicle
HW | Hot Water
IAQ | Indoor Air Quality
RES | Renewable Energy Source
SOC | State Of Charge
TABS | Thermally Activated Building Systems
TBS | Technical Building System
TES | Thermal Energy Storage
VOC | Volatile Organic Compounds

## Building Information
Select your language/Choisissez votre langue/Wähle deine Sprache: | English
Smart Readiness Indicator for Buildings
ASSESSOR INFORMATION
|  | Name | TIMEPAC
|  | Organisation | CYPRUS
Contact information
e-mail address
telephone number (optional)
GENERAL BUILDING INFORMATION
|  | Building type | non-residential
|  | Building usage | non-residential - office
|  | Location | Cyprus
|  | Climate zone: | South Europe
|  | Total useful floor area of the building | 200 - 500 m²
|  | Year of construction | 1960 - 1990
|  | Building state | Renovated
|  | Please provide a brief description of the building | TIMEPAC - InClass Training
|  | Address: | CYPRUS
METHODOLOGY SELECTION
|  | Preferred weightings | Default
|  | Preferred services catalogue | B
Domains present
Are the following technical building systems present in your building?
If not, are they mandatory for new constructions in your country of residence?
1 - This domain is present; 2 - This domain is absent but mandatory; 0 - This domain is absent and not mandatory
|  | Heating | 1
|  | Domestic hot water | 1
|  | Cooling | 1
|  | Ventilation | 1
|  | Lighting | 1
|  | Dynamic building envelope | 0
|  | Electricity | 1
|  | Electric vehicle charging | 0
|  | Monitoring and control | 1
ASSESSMENT DATE
|  | Year | 2024
|  | Month | 9
|  | Day | 23

## _general (hidden)
building type |  | residential | non_residential | triage | Yes | No
|  | single-family house | office |  | (Not applicable) | Yes, mandatory
|  | small multi-family house | educational |  |  | No, not mandatory
|  | large multi-family house | healthcare
|  | other | other
0
1
EU countries |  | Austria | West Europe |  | 2
|  | Belgium | West Europe
|  | Bulgaria | South-East Europe
|  | Croatia | South-East Europe
|  | Cyprus | South Europe
|  | Czech Republic | North-East Europe
|  | Denmark | North Europe
|  | Estonia | North-East Europe
|  | Finland | North Europe
|  | France | West Europe
|  | Germany | West Europe
|  | Greece | South Europe
|  | Hungary | South-East Europe
|  | Iceland | North Europe
|  | Ireland | West Europe
|  | Italy | South Europe
|  | Latvia | North-East Europe
|  | Liechtenstein | West Europe
|  | Lithuania | North-East Europe
|  | Luxembourg | West Europe
|  | Malta | South Europe
|  | Netherlands | West Europe
|  | Norway | North Europe
|  | Poland | North-East Europe
|  | Portugal | South Europe
|  | Romania | South-East Europe
|  | Slovakia | North-East Europe
|  | Slovenia | South-East Europe
|  | Spain | South Europe
|  | Sweden | North Europe
|  | Switzerland | West Europe
|  | United Kingdom | West Europe
|  | non EU | please use user defined weightings!
floor area |  | <200 m²
200 - 500 m²
500 - 1.000 m²
1.000 - 10.000 m²
10.000 - 25.000 m²
> 25.000 m²
age |  | < 1960
1960 - 1990
1990 - 2010
> 2010
not yet constructed
renovated |  | Renovated
Original
weightings |  | Default
User-defined
rows to add to find the right weighting
H | 5
DHW | 6
C | 7
V | 8
L | 9
E | 10
DE | 11
EV | 12
MC | 13
column to find right weighting factor
North Europe | 1
West Europe | 11
South Europe | 21
North-East Europe | 30
South-East Europe | 39
Error message
please enter a valid functionality level
H | 44
DHW | 45
C | 46
V | 47
L | 48
DE | 49
E | 50
EV | 51

## LINK
language | 1 | English | English | Français | Deutsch | Español | Nederlands |  |  | Color Code | From INPUT | Constant | Referenced Value | From Dropdown(index) | Calculated
interface header | 2 | ASSESSOR INFORMATION | ASSESSOR INFORMATION | INFORMATIONS RELATIVES A L'EVALUATEUR | INFORMATIONEN ZUM PRÜFER
interface header | 3 | 0
interface header | 4 | Name | Name | Nom | Name
interface header | 5 | Organisation | Organisation | Organisation | Organisation
interface header | 6 | 0
interface header | 7 | Contact information | Contact information | Coordonnées | Kontaktinformationen
interface header | 8 | e-mail address | e-mail address | adresse électronique | E-Mail Adresse
interface header | 9 | telephone number (optional) | telephone number (optional) | téléphone (facultatif) | Telefonnummer (fakultativ)
interface header | 10 | 0
interface header | 11 | 0
interface header | 12 | 0
interface header | 13 | GENERAL BUILDING INFORMATION | GENERAL BUILDING INFORMATION | INFORMATIONS GENERALES SUR LE BATIMENT | ALLGEMEINE INFORMATIONEN ZUM GEBÄUDE
interface header | 14 | 0
interface header | 15 | Building type | Building type | Type de bâtiment | Gebäudeart
interface header | 16 | Building usage | Building usage | Utilisation du bâtiment | Nutzung des Gebäudes
interface header | 17 | Location | Location | Localisation | Standort
interface header | 18 | Climate zone: | Climate zone: | Zone climatique: | Klimazone:
interface header | 19 | 0
interface header | 20 | Total useful floor area of the building | Total useful floor area of the building | Surface de plancher nette du bâtiment | Gesamtnutzfläche des Gebäudes
interface header | 21 | Year of construction | Year of construction | Année de construction | Jahr der Errichtung
interface header | 22 | Building state | Building state | Etat du bâtiment | Bauzustand
interface header | 23 | 0
interface header | 24 | Please provide a brief description of the building | Please provide a brief description of the building | Brève description du bâtiment: | Bitte geben Sie eine kurze Beschreibung des Gebäudes
interface header | 25 | 0
interface header | 26 | Address: | Address: | Adresse: | Adresse:
interface header | 27 | 0
interface header | 28 | 0
interface header | 29 | METHODOLOGY SELECTION | METHODOLOGY SELECTION | Sélection de la méthodologie | AUSWAHL DER METHODIK
interface header | 30 | Preferred weightings | Preferred weightings | Facteurs de pondération souhaités | Bevorzugte Gewichtungen
interface header | 31 | please make sure to fill in the user-defined weighting factors under the weightings tab! | please make sure to fill in the user-defined weighting factors under the weightings tab! | Veuillez vous assurer de remplir les facteurs de pondération définis par l'utilisateur sous l'onglet 'WEIGHTINGS' | Bitte beachten Sie, dass Sie die benutzerdefinierten Gewichtungsfaktoren auf der Registerkarte "Gewichtungen" eingeben müssen!
interface header | 32 | Preferred services catalogue | Preferred services catalogue | Catalogue de services souhaité | Katalog der bevorzugten Dienstleistungen
interface header | 33 | 0
interface header | 34 | 0
interface header | 35 | Domains present | Domains present | Domaines présents | Vorhandene Bereiche
interface header | 36 | 0
interface header | 37 | Are the following technical building systems present in your building? | Are the following technical building systems present in your building? | Les systèmes techniques suivants sont-ils présents dans le bâtiment? | Sind folgende gebäudetechnischen Anlagen in Ihrem Gebäude vorhanden?
interface header | 38 | If not, are they mandatory for new constructions in your country of residence? | If not, are they mandatory for new constructions in your country of residence? | S'ils ne le sont pas, sont-ils obligatoires pour les nouvelles constructions dans le pays considéré? | Wenn nicht, sind sie für Neubauten in Ihrem Wohnsitzland vorgeschrieben?
interface header | 39 | 0
interface header | 40 | 0
interface header | 41 | Heating | Heating | le chauffage | Heizung
interface header | 42 | Domestic hot water | Domestic hot water | l’eau chaude sanitaire | Warmwasser (Trinkwasser)
interface header | 43 | Cooling | Cooling | le refroidissement | Kühlung
interface header | 44 | Ventilation | Ventilation | la ventilation | Belüftung
interface header | 45 | Lighting | Lighting | l’éclairage | Beleuchtung
interface header | 46 | Dynamic building envelope | Dynamic building envelope | l’enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
interface header | 47 | Electricity | Electricity | l’électricité | Elektrizität
interface header | 48 | Electric vehicle charging | Electric vehicle charging | la recharge des véhicules électriques | Laden von Elektrofahrzeugen
interface header | 49 | Monitoring and control | Monitoring and control | le suivi et le contrôle | Überwachung und Kontrolle
interface header | 50 | 0
interface header | 51 | 0
interface header | 52 | 0
interface header | 53 | HEATING | HEATING | CHAUFFAGE | HEIZUNG
interface header | 54 | 0
interface header | 55 | Emission type | Emission type | Type d'émission | Art der Übergabe
interface header | 56 | Production type | Production type | Type de production | Art der Wärmeerzeugung
interface header | 57 | Thermal energy storage | Thermal energy storage | Stockage d'énergie thermique | Thermische Energiespeicherung
interface header | 58 | Multiple generators | Multiple generators | Générateurs multiples | Mehrere Wärmeerzeuger
interface header | 59 | 0
interface header | 60 | 0
interface header | 61 | 0
interface header | 62 | DOMESTIC HOT WATER | DOMESTIC HOT WATER | EAU CHAUDE SANITAIRE | HAUSHALTSWARMWASSER
interface header | 63 | 0
interface header | 64 | Production type | Production type | Type de production | Art der Wärmeerzeugung
interface header | 65 | Storage present | Storage present | Stockage présent | Warmwasservorhaltung (z.B. Boiler) vorhanden
interface header | 66 | Solar collector | Solar collector | Capteur solaire | Sonnenkollektor (Solarthermie)
interface header | 67 | Multiple generators | Multiple generators | Générateurs multiples | Mehrere Wärmeerzeuger
interface header | 68 | 0
interface header | 69 | 0
interface header | 70 | 0
interface header | 71 | COOLING | COOLING | REFROIDISSEMENT | KÜHLEN
interface header | 72 | 0
interface header | 73 | Emission type | Emission type | Type d'émission | Art der Übergabe
interface header | 74 | Thermal energy storage | Thermal energy storage | Stockage d'énergie thermique | Thermische Energiespeicherung
interface header | 75 | Multiple generators | Multiple generators | Générateurs multiples | Mehrere Kaltwassererzeuger
interface header | 76 | 0
interface header | 77 | 0
interface header | 78 | 0
interface header | 79 | VENTILATION | VENTILATION | VENTILATION | LÜFTUNG
interface header | 80 | 0
interface header | 81 | System type | System type | Type de système | Systemtyp
interface header | 82 | Heat recovery | Heat recovery | Récupération de chaleur | Wärmerückgewinnung
interface header | 83 | Space heating | Space heating | Chauffage des locaux | Raumheizung
interface header | 84 | 0
interface header | 85 | 0
interface header | 86 | 0
interface header | 87 | DYNAMIC ENVELOPE | DYNAMIC ENVELOPE | ENVELOPPE DYNAMIQUE | DYNAMISCHE GEBÄUDEHÜLLE
interface header | 88 | 0
interface header | 89 | Movable shades, screens or blinds | Movable shades, screens or blinds | Protections solaires mobiles | Bewegliche Rollos, Schirme oder Jalousien
interface header | 90 | 0
interface header | 91 | 0
interface header | 92 | 0
interface header | 93 | ELECTRICITY | ELECTRICITY | ELECTRICITE | ELEKTRIZITÄT
interface header | 94 | 0
interface header | 95 | On-site renewable electricity generation | On-site renewable electricity generation | Production d'électricité renouvelable sur site | Stromerzeugung aus erneuerbaren Energien vor Ort
interface header | 96 | Storage of on-site generated renewable electricity | Storage of on-site generated renewable electricity | Stockage de l'électricité renouvelable produite sur site | Speicherung von vor Ort erzeugtem Strom aus erneuerbaren Energien
interface header | 97 | CHP (Combined Heat and Power) | CHP (Combined Heat and Power) | Cogénération | KWK (Kraft-Wärme-Kopplung)
interface header | 98 | 0
interface header | 99 | 0
interface header | 100 | 0
interface header | 101 | ELECTRIC VEHICLE CHARGING | ELECTRIC VEHICLE CHARGING | RECHARGE DES VEHICULES ELECTRIQUES | LADEN VON ELEKTROFAHRZEUGEN
interface header | 102 | 0
interface header | 103 | On-site parking spots | On-site parking spots | Places de stationnement sur place | Vor-Ort-Parkplätze
interface header | 104 | Electric vehicle charging spots | Electric vehicle charging spots | Bornes de recharge pour véhicules électriques | Ladestationen für Elektrofahrzeuge
interface header | 105 | 0
interface dropdown options | 106 | residential | residential | Résidentiel | Wohnen
interface dropdown options | 107 | non-residential | non-residential | Non résidentiel | Nicht-Wohngebäude
interface dropdown options | 108 | residential - single-family house | residential - single-family house | Résidentiel - maison individuelle | Wohnen - Einfamilienhaus
interface dropdown options | 109 | residential - small multi-family house | residential - small multi-family house | Résidentiel - petit collectif | Wohnen - kleines Mehrfamilienhaus
interface dropdown options | 110 | residential - large multi-family house | residential - large multi-family house | Résidentiel - grand collectif | Wohnen - großes Mehrfamilienhaus
interface dropdown options | 111 | residential - other | residential - other | Résidentiel - autre | Wohnen - Sonstiges
interface dropdown options | 112 | non-residential - office | non-residential - office | Non résidentiel - bureaux | Nicht-Wohngebäude - Büro
interface dropdown options | 113 | non-residential - educational | non-residential - educational | Non résidentiel - éducation | Nichtwohngebäude - Bildungseinrichtung
interface dropdown options | 114 | non-residential - healthcare | non-residential - healthcare | Non résidentiel - santé | Nicht-Wohngebäude - Gesundheitswesen
interface dropdown options | 115 | non-residential - other | non-residential - other | Non résidentiel - autre | Nicht-Wohngebäude - Sonstiges
interface dropdown options | 116 | Austria | Austria | Autriche | Österreich
interface dropdown options | 117 | Belgium | Belgium | Belgique | Belgien |  |  | South Europe | C120:C181
interface dropdown options | 118 | Bulgaria | Bulgaria | Bulgarie | Bulgarien
interface dropdown options | 119 | Croatia | Croatia | Croatie | Kroatien
interface dropdown options | 120 | Cyprus | Cyprus | Chypre | Zypern
interface dropdown options | 121 | Czech Republic | Czech Republic | République Tchèque | Tschechische Republik
interface dropdown options | 122 | Denmark | Denmark | Danemark | Dänemark
interface dropdown options | 123 | Estonia | Estonia | Estonie | Estland
interface dropdown options | 124 | Finland | Finland | Finlande | Finnland
interface dropdown options | 125 | France | France | France | Frankreich
interface dropdown options | 126 | Germany | Germany | Allemagne | Deutschland
interface dropdown options | 127 | Greece | Greece | Grèce | Griechenland
interface dropdown options | 128 | Hungary | Hungary | Hongrie | Ungarn
interface dropdown options | 129 | Iceland | Iceland | Islande | Island
interface dropdown options | 130 | Ireland | Ireland | Irlande | Irland
interface dropdown options | 131 | Italy | Italy | Italie | Italien
interface dropdown options | 132 | Latvia | Latvia | Lettonie | Lettland
interface dropdown options | 133 | Liechtenstein | Liechtenstein | Liechtenstein | Liechtenstein
interface dropdown options | 134 | Lithuania | Lithuania | Lituanie | Litauen
interface dropdown options | 135 | Luxembourg | Luxembourg | Luxembourg | Luxemburg
interface dropdown options | 136 | Malta | Malta | Malte | Malta
interface dropdown options | 137 | Netherlands | Netherlands | Pays-Bas | Niederlande
interface dropdown options | 138 | Norway | Norway | Norvège | Norwegen
interface dropdown options | 139 | Poland | Poland | Pologne | Polen
interface dropdown options | 140 | Portugal | Portugal | Portugal | Portugal
interface dropdown options | 141 | Romania | Romania | Roumanie | Rumänien
interface dropdown options | 142 | Slovakia | Slovakia | Slovaquie | Slowakei
interface dropdown options | 143 | Slovenia | Slovenia | Slovénie | Slowenien
interface dropdown options | 144 | Spain | Spain | Espagne | Spanien
interface dropdown options | 145 | Sweden | Sweden | Suède | Schweden
interface dropdown options | 146 | Switzerland | Switzerland | Suisse | Schweiz
interface dropdown options | 147 | United Kingdom | United Kingdom | Royaume-Uni | Vereinigtes Königreich
interface dropdown options | 148 | non EU | non EU | hors Europe | Nicht-EU
interface dropdown options | 149 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 150 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 151 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
interface dropdown options | 152 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
interface dropdown options | 153 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 154 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 155 | North Europe | North Europe | Europe du Nord | Nordeuropa
interface dropdown options | 156 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 157 | North Europe | North Europe | Europe du Nord | Nordeuropa
interface dropdown options | 158 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 159 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 160 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 161 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
interface dropdown options | 162 | North Europe | North Europe | Europe du Nord | Nordeuropa
interface dropdown options | 163 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 164 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 165 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 166 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 167 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 168 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 169 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 170 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 171 | North Europe | North Europe | Europe du Nord | Nordeuropa
interface dropdown options | 172 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 173 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 174 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
interface dropdown options | 175 | North-East Europe | North-East Europe | Europe du Nord-Est | Nordosteuropa
interface dropdown options | 176 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
interface dropdown options | 177 | South Europe | South Europe | Europe du Sud | Südeuropa
interface dropdown options | 178 | North Europe | North Europe | Europe du Nord | Nordeuropa
interface dropdown options | 179 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 180 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
interface dropdown options | 181 | please use user defined weightings! | please use user defined weightings! | Veuillez utiliser les facteurs de pondération définis par l'utilisateur! | Bitte benutzerdefinierte Gewichtungen verwenden!
interface dropdown options | 182 | <200 m² | <200 m² | <200 m² | < 200 m²
interface dropdown options | 183 | 200 - 500 m² | 200 - 500 m² | 200 - 500 m² | 200 - 500 m²
interface dropdown options | 184 | 500 - 1.000 m² | 500 - 1.000 m² | 500 - 1.000 m² | 500 - 1.000 m²
interface dropdown options | 185 | 1.000 - 10.000 m² | 1.000 - 10.000 m² | 1.000 - 10.000 m² | 1.000 - 10.000 m²
interface dropdown options | 186 | 10.000 - 25.000 m² | 10.000 - 25.000 m² | 10.000 - 25.000 m² | 10.000 - 25.000 m²
interface dropdown options | 187 | > 25.000 m² | > 25.000 m² | > 25.000 m² | > 25.000 m²
interface dropdown options | 188 | < 1960 | < 1960 | < 1960 | < 1960
interface dropdown options | 189 | 1960 - 1990 | 1960 - 1990 | 1960 - 1990 | 1960 - 1990
interface dropdown options | 190 | 1990 - 2010 | 1990 - 2010 | 1990 - 2010 | 1990 - 2010
interface dropdown options | 191 | > 2010 | > 2010 | > 2010 | > 2010
interface dropdown options | 192 | not yet constructed | not yet constructed | Non encore construit | Noch nicht gebaut
interface dropdown options | 193 | Renovated | Renovated | Rénové | Renoviert
interface dropdown options | 194 | Original | Original | Initial | Urspungszustand
interface dropdown options | 195 | Default | Default | Par défaut | Standard
interface dropdown options | 196 | User-defined | User-defined | Définis par l'utilisateur | Benutzerdefiniert
interface dropdown options | 197 | A | A | A | A
interface dropdown options | 198 | B | B | B | B
interface dropdown options | 199 | Custom services mix | Custom services mix | Mix de services sur-mesure | Benutzerdefiniert
overview of services | 200 | Domain | Domain | Domaine | Bereich
overview of services | 201 | 0
overview of services | 202 | 0
overview of services | 203 | Heating | Heating | Chauffage | Heizung
overview of services | 204 | Heating | Heating | Chauffage | Heizung
overview of services | 205 | Heating | Heating | Chauffage | Heizung
overview of services | 206 | Heating | Heating | Chauffage | Heizung
overview of services | 207 | Heating | Heating | Chauffage | Heizung
overview of services | 208 | Heating | Heating | Chauffage | Heizung
overview of services | 209 | Heating | Heating | Chauffage | Heizung
overview of services | 210 | Heating | Heating | Chauffage | Heizung
overview of services | 211 | Heating | Heating | Chauffage | Heizung
overview of services | 212 | Heating | Heating | Chauffage | Heizung
overview of services | 213 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
overview of services | 214 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
overview of services | 215 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
overview of services | 216 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
overview of services | 217 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
overview of services | 218 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 219 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 220 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 221 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 222 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 223 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 224 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 225 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 226 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 227 | Cooling | Cooling | Refroidissement | Kühlung
overview of services | 228 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 229 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 230 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 231 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 232 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 233 | Ventilation | Ventilation | Ventilation | Belüftung
overview of services | 234 | Lighting | Lighting | Eclairage | Beleuchtung
overview of services | 235 | Lighting | Lighting | Eclairage | Beleuchtung
overview of services | 236 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
overview of services | 237 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
overview of services | 238 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
overview of services | 239 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 240 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 241 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 242 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 243 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 244 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 245 | Electricity | Electricity | Electricité | Elektrizität
overview of services | 246 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
overview of services | 247 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
overview of services | 248 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
overview of services | 249 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 250 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 251 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 252 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 253 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 254 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 255 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 256 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
overview of services | 257 | Code | Code | Code | Code
overview of services | 258 | 0
overview of services | 259 | 0
overview of services | 260 | H-1a | H-1a | H-1a | H-1a
overview of services | 261 | H-1b | H-1b | H-1b | H-1b
overview of services | 262 | H-1c | H-1c | H-1c | H-1c
overview of services | 263 | H-1d | H-1d | H-1d | H-1d
overview of services | 264 | H-1f | H-1f | H-1f | H-1f
overview of services | 265 | H-2a | H-2a | H-2a | H-2a
overview of services | 266 | H-2b | H-2b | H-2b | H-2b
overview of services | 267 | H-2d | H-2d | H-2d | H-2d
overview of services | 268 | H-3 | H-3 | H-3 | H-3
overview of services | 269 | H-4 | H-4 | H-4 | H-4
overview of services | 270 | DHW-1a | DHW-1a | DHW-1a | DHW-1a
overview of services | 271 | DHW-1b | DHW-1b | DHW-1b | DHW-1b
overview of services | 272 | DHW-1d | DHW-1d | DHW-1d | DHW-1d
overview of services | 273 | DHW-2b | DHW-2b | DHW-2b | DHW-2b
overview of services | 274 | DHW-3 | DHW-3 | DHW-3 | DHW-3
overview of services | 275 | C-1a | C-1a | C-1a | C-1a
overview of services | 276 | C-1b | C-1b | C-1b | C-1b
overview of services | 277 | C-1c | C-1c | C-1c | C-1c
overview of services | 278 | C-1d | C-1d | C-1d | C-1d
overview of services | 279 | C-1f | C-1f | C-1f | C-1f
overview of services | 280 | C-1g | C-1g | C-1g | C-1g
overview of services | 281 | C-2a | C-2a | C-2a | C-2a
overview of services | 282 | C-2b | C-2b | C-2b | C-2b
overview of services | 283 | C-3 | C-3 | C-3 | C-3
overview of services | 284 | C-4 | C-4 | C-4 | C-4
overview of services | 285 | V-1a | V-1a | V-1a | V-1a
overview of services | 286 | V-1c | V-1c | V-1c | V-1c
overview of services | 287 | V-2c | V-2c | V-2c | V-2c
overview of services | 288 | V-2d | V-2d | V-2d | V-2d
overview of services | 289 | V-3 | V-3 | V-3 | V-3
overview of services | 290 | V-6 | V-6 | V-6 | V-6
overview of services | 291 | L-1a | L-1a | L-1a | L-1a
overview of services | 292 | L-2 | L-2 | L-2 | L-2
overview of services | 293 | DE-1 | DE-1 | DE-1 | DE-1
overview of services | 294 | DE-2 | DE-2 | DE-2 | DE-2
overview of services | 295 | DE-4 | DE-4 | DE-4 | DE-4
overview of services | 296 | E-2 | E-2 | E-2 | E-2
overview of services | 297 | E-3 | E-3 | E-3 | E-3
overview of services | 298 | E-4 | E-4 | E-4 | E-4
overview of services | 299 | E-5 | E-5 | E-5 | E-5
overview of services | 300 | E-8 | E-8 | E-8 | E-8
overview of services | 301 | E-11 | E-11 | E-11 | E-11
overview of services | 302 | E-12 | E-12 | E-12 | E-12
overview of services | 303 | EV-15 | EV-15 | EV-15 | EV-15
overview of services | 304 | EV-16 | EV-16 | EV-16 | EV-16
overview of services | 305 | EV-17 | EV-17 | EV-17 | EV-17
overview of services | 306 | MC-3 | MC-3 | MC-3 | MC-3
overview of services | 307 | MC-4 | MC-4 | MC-4 | MC-4
overview of services | 308 | MC-9 | MC-9 | MC-9 | MC-9
overview of services | 309 | MC-13 | MC-13 | MC-13 | MC-13
overview of services | 310 | MC-25 | MC-25 | MC-25 | MC-25
overview of services | 311 | MC-28 | MC-28 | MC-28 | MC-28
overview of services | 312 | MC-29 | MC-29 | MC-29 | MC-29
overview of services | 313 | MC-30 | MC-30 | MC-30 | MC-30
overview of services | 314 | Service group | Service group | Groupe de services | Dienstgruppe
overview of services | 315 | 0
overview of services | 316 | 0
overview of services | 317 | Heat control - demand side | Heat control - demand side | Régulation du chauffage - côté utilisateur | Wärmesteuerung - Bedarfsabhängige
overview of services | 318 | Heat control - demand side | Heat control - demand side | Régulation du chauffage - côté utilisateur | Wärmesteuerung - Bedarfsabhängige
overview of services | 319 | Heat control - demand side | Heat control - demand side | Régulation du chauffage - côté utilisateur | Wärmesteuerung - Bedarfsabhängige
overview of services | 320 | Heat control - demand side | Heat control - demand side | Régulation du chauffage - côté utilisateur | Wärmesteuerung - Bedarfsabhängige
overview of services | 321 | Heat control - demand side | Heat control - demand side | Régulation du chauffage - côté utilisateur | Wärmesteuerung - Bedarfsabhängige
overview of services | 322 | Control heat production facilities | Control heat production facilities | Régulation des installations de production de chaleur | Kontrolle von Wärmeerzeugungsanlagen
overview of services | 323 | Control heat production facilities | Control heat production facilities | Régulation des installations de production de chaleur | Kontrolle von Wärmeerzeugungsanlagen
overview of services | 324 | Control heat production facilities | Control heat production facilities | Régulation des installations de production de chaleur | Kontrolle von Wärmeerzeugungsanlagen
overview of services | 325 | Information to occupants and facility managers | Information to occupants and facility managers | Information aux occupants et au gestionnaire du bâtiment | Informationen für Bewohner und Gebäudeverwalter
overview of services | 326 | Flexibility and grid interaction | Flexibility and grid interaction | Flexibilité et interaction avec le réseau | Flexibilität und Netzinteraktion
overview of services | 327 | Control DHW production facilities | Control DHW production facilities | Régulation des installations de production d'eau chaude sanitaire | Kontrolle der Warmwasserbereitungsanlagen
overview of services | 328 | Control DHW production facilities | Control DHW production facilities | Régulation des installations de production d'eau chaude sanitaire | Kontrolle der Warmwasserbereitungsanlagen
overview of services | 329 | Control DHW production facilities | Control DHW production facilities | Régulation des installations de production d'eau chaude sanitaire | Kontrolle der Warmwasserbereitungsanlagen
overview of services | 330 | Control DHW production facilities | Control DHW production facilities | Régulation des installations de production d'eau chaude sanitaire | Kontrolle der Warmwasserbereitungsanlagen
overview of services | 331 | Information to occupants and facility managers | Information to occupants and facility managers | Information aux occupants et au gestionnaire du bâtiment | Informationen für Bewohner und Gebäudeverwalter
overview of services | 332 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 333 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 334 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 335 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 336 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 337 | Cooling control - demand side | Cooling control - demand side | Régulation du refroidissement - côté utilisateur | Kühlungssteuerung - Bedarfsabhängige
overview of services | 338 | Control cooling production facilities | Control cooling production facilities | Régulation des installations de production de froid | Kontrolle der Kühlunganlagen
overview of services | 339 | Control cooling production facilities | Control cooling production facilities | Régulation des installations de production de froid | Kontrolle der Kühlunganlagen
overview of services | 340 | Information to occupants and facility managers | Information to occupants and facility managers | Information aux occupants et au gestionnaire du bâtiment | Informationen für Bewohner und Gebäudeverwalter
overview of services | 341 | Flexibility and grid interaction | Flexibility and grid interaction | Flexibilité et intéraction avec le réseau | Flexibilität und Netzinteraktion
overview of services | 342 | Air flow control | Air flow control | Régulation du flux d'air | Steuerung des Luftstroms
overview of services | 343 | Air flow control | Air flow control | Régulation du flux d'air | Steuerung des Luftstroms
overview of services | 344 | Air temperature control | Air temperature control | Régulation de la température de l'air | Kontrolle der Lufttemperatur
overview of services | 345 | Air temperature control | Air temperature control | Régulation de la température de l'air | Kontrolle der Lufttemperatur
overview of services | 346 | Free cooling | Free cooling | Refroidissement naturel | Freie (Passiv-)Kühlung
overview of services | 347 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 348 | Artificial lighting control | Artificial lighting control | Commande de l'éclairage artificiel | Steuerung der künstlichen Beleuchtung
overview of services | 349 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | Régulation de l'intensité lumineuse en fonction de la lumière naturelle | Steuerung der künstlichen Beleuchtung in Abhängigkeit vom Tageslicht
overview of services | 350 | Window control | Window control | Commande des fenêtres | Fenstersteuerung
overview of services | 351 | Window control | Window control | Commande des fenêtres | Fenstersteuerung
overview of services | 352 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 353 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 354 | DER - Storage | DER - Storage | Production d'électricité décentralisée - Stockage | Stromerzeugung - Speicherung
overview of services | 355 | DER- Optimization | DER- Optimization | Production d'électricité décentralisée - Optimisation | Stromerzeugung - Optimierung
overview of services | 356 | DER - Generation Control | DER - Generation Control | Production d'électricité décentralisée - Commande de la production | Stromerzeugung - Steuerung der Erzeugung
overview of services | 357 | DSM- Storage | DSM- Storage | Flexibilité de la demande - Stockage | DSM - Speicherung
overview of services | 358 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 359 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 360 | EV Charging | EV Charging | Recharge EV | EV - Laden
overview of services | 361 | EV Charging - Grid | EV Charging - Grid | Recharge EV - réseau | EV - Laden - Netz
overview of services | 362 | EV Charging - connectivity | EV Charging - connectivity | Recharge EV - connectivité | EV - Laden - Konnektivität
overview of services | 363 | HVAC interaction control | HVAC interaction control | Contrôle de systèmes CVC | HLK-Interaktionssteuerung
overview of services | 364 | Fault detection | Fault detection | Détection des défauts | Fehlersuche
overview of services | 365 | TBS interaction control | TBS interaction control | Contrôle de systèmes techniques du bâtiment | TBS-Interaktionskontrolle
overview of services | 366 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 367 | Smart Grid Integration | Smart Grid Integration | Intégration avec le réseau intelligent | Integration intelligenter Stromnetze
overview of services | 368 | Feedback - Reporting information | Feedback - Reporting information | Remontée d'informations | Feedback - Informationen melden
overview of services | 369 | Override control | Override control | Préemption du contrôle | Vorrangige Kontrolle
overview of services | 370 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Plateforme unique permettant le contrôle automatique et la coordination entre les systèmes techniques du bâtiment + optimisation des flux d'énergie en fonction de l'occupation, de la météo et des ordres reçus de la part du réseau | Eine einzige Plattform, die eine automatische Steuerung und Koordinierung zwischen den TBS sowie eine Optimierung des Energieflusses auf der Grundlage von Belegung, Wetter und Netzsignalen ermöglicht.
overview of services | 371 | Smart ready service | Smart ready service | Service à potentiel d'intelligence | Smart ready service
overview of services | 372 | 0
overview of services | 373 | 0
overview of services | 374 | Heat emission control | Heat emission control | Régulation de l'émission | Regelung der Wärmeabgabe
overview of services | 375 | Emission control for TABS (heating mode) | Emission control for TABS (heating mode) | Régulation d'émission pour système thermo-actif - mode de chauffage (par exemple, plancher chauffant) | Regelung der Übergabe für TABS (Heizbetrieb)
overview of services | 376 | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | Régulation de la température du fluide caloporteur (en départ ou en retour, air ou eau) . | Regelung der Temperatur des Verteilungsmediums (Zu- oder Abluft- oder Wasserdurchfluss) - Eine ähnliche Funktion kann für die Regelung von direkten elektrischen Heiznetzen angewendet werden.
overview of services | 377 | Control of distribution pumps in networks | Control of distribution pumps in networks | Commande des pompes de distribution dans les réseaux | Steuerung von Verteilerpumpen in Netzen
overview of services | 378 | Thermal Energy Storage (TES) for building heating (excluding TABS) | Thermal Energy Storage (TES) for building heating (excluding TABS) | Stockage d'énergie thermique pour le chauffage du bâtiment (hors systèmes thermoactifs - TABS) | Thermische Energiespeicher (TES) für die Gebäudeheizung (ohne TABS)
overview of services | 379 | Heat generator control (all except heat pumps) | Heat generator control (all except heat pumps) | Commande de générateurs de chaleur (PAC exceptées) | Steuerung des Wärmeerzeugers (alle außer Wärmepumpen)
overview of services | 380 | Heat generator control (for heat pumps) | Heat generator control (for heat pumps) | Commande de la production de chaleur par les PAC | Steuerung des Wärmeerzeugers (für Wärmepumpen)
overview of services | 381 | Sequencing in case of different heat generators | Sequencing in case of different heat generators | Régulation en cascade (ordre de priorité) des différentes sources de production de chaleur | Reihenfolge bei unterschiedlichen Wärmeerzeugern
overview of services | 382 | Report information regarding heating system performance | Report information regarding heating system performance | Remontée d'informations sur la performance du système de chauffage | Informationen über die Leistung der Heizungsanlage melden
overview of services | 383 | Flexibility and grid interaction | Flexibility and grid interaction | Flexibilité et intéraction avec le réseau | Flexibilität und Netzinteraktion
overview of services | 384 | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | Régulation de la température de stockage de l’eau chaude sanitaire avec chauffage électrique intégré ou pompe à chaleur électrique | Steuerung der DHW Speicheraufladung (mit direkter elektrischer Heizung oder integrierter elektrischer Wärmepumpe)
overview of services | 385 | Control of DHW storage charging (using hot water generation) | Control of DHW storage charging (using hot water generation) | Régulation de la température de stockage d’eau chaude sanitaire en utilisant un générateur d’eau chaude | Steuerung der DHW Speicheraufladung (durch Warmwassererzeugung)
overview of services | 386 | Control of DHW storage charging (with solar collector and supplymentary heat generation) | Control of DHW storage charging (with solar collector and supplymentary heat generation) | Régulation de la température de stockage d’eau chaude sanitaire avec collecteur d’énergie solaire et génération de chaleur complémentaire | Steuerung der DHW Speicheraufladung (mit Solarkollektor/Solarthermie und Zusatzwärmeerzeugung)
overview of services | 387 | Sequencing in case of different DHW generators | Sequencing in case of different DHW generators | Régulation en cascade des différentes sources de production d'eau chaude sanitaire | Reihenfolge bei unterschiedlichen Warmwassererzeugern
overview of services | 388 | Report information regarding domestic hot water performance | Report information regarding domestic hot water performance | Remontée d'informations sur la performance du système d'eau chaude sanitaire | Informationen über die Leistung der Warmwasserbereitung melden
overview of services | 389 | Cooling emission control | Cooling emission control | Régulation de l'émission | Regelung der Übergabe beim Kühlen
overview of services | 390 | Emission control for TABS (cooling mode) | Emission control for TABS (cooling mode) | Régulation d'émission pour système thermo-actif - mode refroidissement | Regelung der Übergabe für TABS (Kühlbetrieb)
overview of services | 391 | Control of distribution network chilled water temperature (supply or return) | Control of distribution network chilled water temperature (supply or return) | Régulation de la température de l’eau glacée du réseau de distribution (en départ ou en retour) | Regelung der Kaltwassertemperatur im Verteilungsnetz (Vorlauf oder Rücklauf)
overview of services | 392 | Control of distribution pumps in networks | Control of distribution pumps in networks | Commande des pompes de distribution dans les réseaux | Steuerung von Verteilerpumpen in Netzen
overview of services | 393 | Interlock: avoiding simultaneous heating and cooling in the same room | Interlock: avoiding simultaneous heating and cooling in the same room | Asservissement entre la régulation du chauffage et celle du refroidissement (pour éviter de chauffer et refroidir simultanément la même pièce) | Schaltsperre: Vermeidung von gleichzeitigem Heizen und Kühlen im selben Raum
overview of services | 394 | Control of Thermal Energy Storage (TES) operation | Control of Thermal Energy Storage (TES) operation | Régulation du stockage d'énergie thermique | Steuerung des Betriebs von thermischen Energiespeichern (TES)
overview of services | 395 | Generator control for cooling | Generator control for cooling | Régulation du générateur pour le refroidissement | Generatorsteuerung für die Kühlung
overview of services | 396 | Sequencing of different cooling generators | Sequencing of different cooling generators | Régulation en cascade des différentes sources de production de froid | Reihenfolge der verschiedenen Kälteerzeuger
overview of services | 397 | Report information regarding cooling system performance | Report information regarding cooling system performance | Remontée d'informations sur la performance du système de refroidissement | Informationen über die Leistung des Kühlsystems melden
overview of services | 398 | Flexibility and grid interaction | Flexibility and grid interaction | Flexibilité et intéraction avec le réseau | Flexibilität und Netzinteraktion
overview of services | 399 | Supply air flow control at the room level | Supply air flow control at the room level | Régulation de l'alimentation en air au niveau de la pièce | Regelung des Zuluftstroms auf der Raumebene
overview of services | 400 | Air flow or pressure control at the air handler level | Air flow or pressure control at the air handler level | Régulation du débit d’air ou de la pression au niveau de la centrale de traitement d’air | Luftstrom- oder Druckregelung auf der Ebene der Lüftungsanlage
overview of services | 401 | Heat recovery control: prevention of overheating | Heat recovery control: prevention of overheating | Commande de récupération de chaleur : prévention des surchauffes | Vermeidung von Überhitzung
overview of services | 402 | Supply air temperature control at the air handling unit level | Supply air temperature control at the air handling unit level | Régulation de la température de l'air ambiant au niveau de l'unité de traitement de l'air | Regelung der Zulufttemperatur auf der Ebene des Lüftungsgeräts
overview of services | 403 | Free cooling with mechanical ventilation system | Free cooling with mechanical ventilation system | Refroidissement mécanique naturel | Freie Kühlung mit mechanischem Belüftungssystem
overview of services | 404 | Reporting information regarding IAQ | Reporting information regarding IAQ | Remontée d'informations sur la qualité de l'air intérieur | Meldung von Informationen über IAQ
overview of services | 405 | Occupancy control for indoor lighting | Occupancy control for indoor lighting | Commande basée sur l’occupation | Belegungssteuerung für die Innenbeleuchtung
overview of services | 406 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | Régulation de l'intensité lumineuse en fonction de la lumière naturelle | Steuerung der Leistung der künstlichen Beleuchtung in Abhängigkeit vom Tageslicht
overview of services | 407 | Window solar shading control | Window solar shading control | Commande de la protection solaire des fenêtres | Sonnenschutz für Fenster
overview of services | 408 | Window open/closed control, combined with HVAC system | Window open/closed control, combined with HVAC system | Commande d'ouverture/fermeture des fenêtres, combinée avec le système CVC | Steuerung des Öffnens und Schließens von Fenstern, kombiniert mit HLK-System
overview of services | 409 | Reporting information regarding performance of dynamic building envelope systems | Reporting information regarding performance of dynamic building envelope systems | Remontée d'informations sur les performances des systèmes d'enveloppe dynamique du bâtiment | Berichterstattung über die Leistung von dynamischen Gebäudehüllensystemen
overview of services | 410 | Reporting information regarding local electricity generation | Reporting information regarding local electricity generation | Remontée d'informations sur la production locale d'électricté | Meldung von Informationen über die lokale Stromerzeugung
overview of services | 411 | Storage of (locally generated) electricity | Storage of (locally generated) electricity | Stockage de l'électricité (produite localement) | Speicherung von (lokal erzeugtem) Strom
overview of services | 412 | Optimizing self-consumption of locally generated electricity | Optimizing self-consumption of locally generated electricity | Optimisation de l'autoconsommation de l'électricité produite localement | Optimierung des Eigenverbrauchs von lokal erzeugtem Strom
overview of services | 413 | Control of combined heat and power plant (CHP) | Control of combined heat and power plant (CHP) | Commande de la cogénération | Steuerung von Kraft-Wärme-Kopplungsanlagen (KWK)
overview of services | 414 | Support of (micro)grid operation modes | Support of (micro)grid operation modes | Soutien à l'opération du (micro)réseau | Unterstützung von (Mikro-)Netzbetriebsarten
overview of services | 415 | Reporting information regarding energy storage | Reporting information regarding energy storage | Remontée d'informations sur le stockage d'énergie | Meldung von Informationen über die Energiespeicherung
overview of services | 416 | Reporting information regarding electricity consumption | Reporting information regarding electricity consumption | Remontée d'informations sur la consommation d'électricité | Meldung von Informationen über den Stromverbrauch
overview of services | 417 | EV Charging Capacity | EV Charging Capacity | Capacité de charge des VE | EV-Ladekapazität
overview of services | 418 | EV Charging Grid balancing | EV Charging Grid balancing | Capacité de charge des VE, équilibrage réseau | EV-Laden Netzausgleich
overview of services | 419 | EV charging information and connectivity | EV charging information and connectivity | Capacité de charge des VE, information et connectivité | Informationen zum Laden von Elektrofahrzeugen und Anschlussmöglichkeiten
overview of services | 420 | Run time management of HVAC systems | Run time management of HVAC systems | Gestion temporelle des systèmes CVC | Laufzeitmanagement von HLK-Systemen
overview of services | 421 | Detecting faults of technical building systems and providing support to the diagnosis of these faults | Detecting faults of technical building systems and providing support to the diagnosis of these faults | Détection des défauts des systèmes techniques du bâtiment et aide au diagnostic | Erkennen von Fehlern an gebäudetechnischen Anlagen und Unterstützung bei der Diagnose dieser Fehler
overview of services | 422 | Occupancy detection: connected services | Occupancy detection: connected services | Détection d'occupation: services connectés | Belegungserkennung: vernetzte Dienste
overview of services | 423 | Central reporting of TBS performance and energy use | Central reporting of TBS performance and energy use | Remontée d'information centralisée sur la performance et l'utilisation d'énergie des systèmes techniques du bâtiment | Zentrale Berichterstattung über TBS-Leistung und Energieverbrauch
overview of services | 424 | Smart Grid Integration | Smart Grid Integration | Intégration au réseau intelligent | Integration intelligenter Stromnetze
overview of services | 425 | Reporting information regarding demand side management performance and operation | Reporting information regarding demand side management performance and operation | Remontée d'informations sur le fonctionnement et la performance de la gestion de la demande (effacements) | Berichterstattung über die Leistung und den Betrieb der Bedarfssteuerung
overview of services | 426 | Override of DSM control | Override of DSM control | Préemption du contrôle de gestion de la demande | Außerkraftsetzen der DSM-Steuerung
overview of services | 427 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Plateforme unique permettant le contrôle automatique et la coordination entre les systèmes techniques du bâtiment + optimisation des flux d'énergie en fonction de l'occupation, de la météo et des ordres reçus de la part du réseau | Eine einzige Plattform, die eine automatische Steuerung und Koordinierung zwischen den TBS sowie eine Optimierung des Energieflusses auf der Grundlage von Belegung, Wetter und Netzsignalen ermöglicht.
overview of services | 428 | Functionality level 0 (as non-smart default) | Functionality level 0 (as non-smart default) | Niveau de fonctionnalité 0 (non intelligent, par défaut) | Funktionalitätsebene 0 (als nicht-smarte Voreinstellung)
overview of services | 429 | 0
overview of services | 430 | 0
overview of services | 431 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 432 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 433 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 434 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 435 | Continuous storage operation | Continuous storage operation | Stockage continu | Betrieb mit dauerhafter Speicherung
overview of services | 436 | Constant temperature control | Constant temperature control | Régulation de température constante | Konstante Temperaturregelung
overview of services | 437 | On/Off-control of heat generator | On/Off-control of heat generator | Commande de mise en marche/arrêt du générateur de chaleur | On/Off-Steuerung des Wärmeerzeugers
overview of services | 438 | Priorities only based on running time | Priorities only based on running time | Priorités uniquement basées sur le temps de fonctionnement | Prioritäten nur auf Basis der Laufzeit
overview of services | 439 | None | None | Aucune | Keine
overview of services | 440 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 441 | Automatic control on / off | Automatic control on / off | Commande automatique de mise en marche/arrêt | Automatische Steuerung ein/aus
overview of services | 442 | Automatic control on / off | Automatic control on / off | Commande automatique de mise en marche/arrêt | Automatische Steuerung ein/aus
overview of services | 443 | Manual selected control of solar energy or heat generation | Manual selected control of solar energy or heat generation | Commande manuelle de la source de chauffe | Manuell gewählte Steuerung von Solarenergie oder Wärmeerzeugung
overview of services | 444 | Priorities only based on running time | Priorities only based on running time | Priorités uniquement basées sur le temps de fonctionnement | Prioritäten nur auf Basis der Laufzeit
overview of services | 445 | None | None | Aucune | Keine
overview of services | 446 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 447 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 448 | Constant temperature control | Constant temperature control | Régulation de température constante | Konstante Temperaturregelung
overview of services | 449 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 450 | No interlock | No interlock | Aucun asservissement | Keine Verriegelung
overview of services | 451 | Continuous storage operation | Continuous storage operation | Stockage continu | Kontinuierlicher Speicherbetrieb
overview of services | 452 | On/Off-control of cooling production | On/Off-control of cooling production | Commande de mise en marche/arrêt du générateur de froid | On/Off-Steuerung der Kälteerzeugung
overview of services | 453 | Priorities only based on running times | Priorities only based on running times | Priorités uniquement basées sur le temps de fonctionnement | Prioritäten nur auf Basis der Laufzeiten
overview of services | 454 | None | None | Aucune | Keine
overview of services | 455 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 456 | No ventilation system or manual control | No ventilation system or manual control | Pas de système de ventilation, ou commande manuelle | Kein Belüftungssystem oder manuelle Steuerung
overview of services | 457 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | Aucune régulation automatique : fournit en continu un débit d'air pour une charge maximale pour toutes les pièces | Keine automatische Steuerung: Kontinuierliche Zufuhr des Luftstroms für eine maximale Belüftung aller Räume
overview of services | 458 | Without overheating control | Without overheating control | Sans régulation de surchauffe | Ohne Überhitzungskontrolle
overview of services | 459 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 460 | No automatic control | No automatic control | Aucune régulation automatique | Keine automatische Regelung
overview of services | 461 | None | None | Aucune | Keine
overview of services | 462 | Manual on/off switch | Manual on/off switch | Interrupteur manuel de mise en marche/arrêt | Manueller Ein/Aus-Schalter
overview of services | 463 | Manual (central) | Manual (central) | Manuelle centralisée | Manuell (zentral)
overview of services | 464 | No sun shading or only manual operation | No sun shading or only manual operation | Pas de protection solaire ou ouverture/fermeture manuelle | Kein Sonnenschutz oder nur manuelle Bedienung
overview of services | 465 | Manual operation or only fixed windows | Manual operation or only fixed windows | Ouverture/fermeture manuelle ou fenêtres fixes seulement | Manuelle Bedienung oder nur feste Fenster
overview of services | 466 | No reporting | No reporting | Pas de remontée d'information | Keine Berichterstattung
overview of services | 467 | None | None | Aucun | Keine
overview of services | 468 | None | None | Aucun | Keine
overview of services | 469 | None | None | Aucun | Keine
overview of services | 470 | CHP control based on scheduled runtime management and/or current heat energy demand | CHP control based on scheduled runtime management and/or current heat energy demand | Contrôle de la cogénération sur la base d'un fonctionnement programmé et/ou sur la base de la demande de chaleur | KWK-Steuerung auf der Grundlage des geplanten Laufzeitmanagements und/oder des aktuellen Wärmeenergiebedarfs
overview of services | 471 | None | None | Aucun | Keine
overview of services | 472 | None | None | Aucun | Keine
overview of services | 473 | None | None | Aucun | Keine
overview of services | 474 | not present | not present | Non présente | nicht vorhanden
overview of services | 475 | Not present (uncontrolled charging) | Not present (uncontrolled charging) | Non présente (charge non contrôlée) | Nicht vorhanden (unkontrollierte Aufladung)
overview of services | 476 | No information available | No information available | Pas d'information disponible | Keine Informationen verfügbar
overview of services | 477 | Manual setting | Manual setting | Configuration manuelle | Manuelle Einstellung
overview of services | 478 | No central indication of detected faults and alarms | No central indication of detected faults and alarms | Aucune indication centralisée des défauts détectés et des alarmes | Keine zentrale Anzeige von erkannten Fehlern und Alarmen
overview of services | 479 | None | None | Aucun | Keine
overview of services | 480 | None | None | Aucun | Keine
overview of services | 481 | None - No harmonization between grid and TBS; building is operated independently from the grid load | None - No harmonization between grid and TBS; building is operated independently from the grid load | cla | Keine - Keine Harmonisierung zwischen Netz und TBS; Gebäude wird unabhängig von der Netzlast betrieben
overview of services | 482 | None | None | Aucune | Keine
overview of services | 483 | No DSM control | No DSM control | Pas de gestion de la demande | Keine DSM-Kontrolle
overview of services | 484 | None | None | Aucune | Keine
overview of services | 485 | Functionality level 1 | Functionality level 1 | Niveau de fonctionnalité 1 | Funktionalitätsstufe 1
overview of services | 486 | 0
overview of services | 487 | 0
overview of services | 488 | Central automatic control (e.g. central thermostat) | Central automatic control (e.g. central thermostat) | Régulation centrale automatique (par exemple, thermostat centralisé) | Zentrale automatische Steuerung (z. B. zentraler Thermostat)
overview of services | 489 | Central automatic control | Central automatic control | Régulation centrale automatique | Zentrale automatische Steuerung
overview of services | 490 | Outside temperature compensated control | Outside temperature compensated control | Régulation compensée en fonction de la température extérieure | Außentemperaturkompensierte Steuerung
overview of services | 491 | On off control | On off control | Commande automatique de mise en marche/arrêt | Ein-Aus-Steuerung
overview of services | 492 | Time-scheduled storage operation | Time-scheduled storage operation | Stockage géré par plage horaire | Zeitgesteuerter Speicherbetrieb
overview of services | 493 | Variable temperature control depending on outdoor temperature | Variable temperature control depending on outdoor temperature | Régulation de température variable en fonction de la température extérieure | Variable Temperaturregelung in Abhängigkeit von der Außentemperatur
overview of services | 494 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Régulation multi-niveaux de la capacité des générateurs de chaleur en fonction de la charge ou de la demande (par exemple marche/arrêt de plusieurs compresseurs) | Mehrstufige Steuerung der Wärmeerzeugerleistung in Abhängigkeit von der Last oder dem Bedarf (z. B. Ein- und Ausschalten mehrerer Verdichter)
overview of services | 495 | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to fixed priority list: e.g. based on rated energy efficiency | Régulation basée sur une liste de priorités (par exemple, selon l'efficacité énergétique) | Steuerung nach fester Prioritätenliste: z. B. auf der Grundlage der bewerteten Energieeffizienz
overview of services | 496 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Remontée centralisée ou déportée d'indicateurs temps réel de performance (température, sous-comptage) | Zentrale oder ferngesteuerte Berichterstattung über aktuelle Leistungskennzahlen (z. B. Temperaturen, Submetering-Energieverbrauch)
overview of services | 497 | Scheduled operation of heating system | Scheduled operation of heating system | Programmation des plages de fonctionnement du système de chauffage | Planmäßiger Betrieb der Heizungsanlage
overview of services | 498 | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable | Commande automatique de mise en marche/arrêt et programmation du temps de charge | Automatisches Ein- und Ausschalten und zeitgesteuertes Laden möglich
overview of services | 499 | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable | Commande automatique de mise en marche/arrêt et programmation du temps de charge | Automatisches Ein- und Ausschalten und zeitgesteuertes Laden möglich
overview of services | 500 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Commande automatique de la charge de stockage d’énergie solaire (Priorité 1) et charge de stockage supplémentaire (priorité 2) | Automatische Steuerung der Solarspeicherladung (Prio. 1) und der zusätzlichen Speicherladung
overview of services | 501 | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to fixed priority list: e.g. based on rated energy efficiency | Régulation basée sur une liste de priorités (par exemple, selon l'efficacité énergétique) | Steuerung nach fester Prioritätenliste: z. B. auf der Grundlage der bewerteten Energieeffizienz
overview of services | 502 | Indication of actual values (e.g. temperatures, submetering energy usage) | Indication of actual values (e.g. temperatures, submetering energy usage) | Indication des valeurs réelles uniquement (par exemple, températures, valeurs mesurées) | Anzeige von Ist-Werten (z. B. Temperaturen, Submetering-Energieverbrauch)
overview of services | 503 | Central automatic control | Central automatic control | Régulation centrale automatique | Zentrale automatische Steuerung
overview of services | 504 | Central automatic control | Central automatic control | Régulation centrale automatique | Zentrale automatische Steuerung
overview of services | 505 | Outside temperature compensated control | Outside temperature compensated control | Régulation compensée en fonction de la température extérieure | Außentemperaturkompensierte Steuerung
overview of services | 506 | On off control | On off control | Commande automatique de mise en marche/arrêt | Ein-Aus-Steuerung
overview of services | 507 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Asservissement partiel (minimisant la possibilité d'un chauffage et d'un refroidissement simultanés, par exemple en définissant un point de consigne variable) | Teilweise Verriegelung (Minimierung des Risikos von gleichzeitigem Heizen und Kühlen, z.B. durch gleitende Sollwerte)
overview of services | 508 | Time-scheduled storage operation | Time-scheduled storage operation | Stockage géré par plage horaire | Zeitgesteuerter Speicherbetrieb
overview of services | 509 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Régulation multi-niveaux de la capacité des générateurs de froid en fonction de la charge ou de la demande (par exemple marche/arrêt de plusieurs compresseurs) | Mehrstufige Steuerung der Kälteerzeugungsleistung in Abhängigkeit von der Last oder dem Bedarf (z. B. Ein- und Ausschalten mehrerer Verdichter)
overview of services | 510 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Ordre de priorité fixe uniquement basé sur les charges : par exemple en fonction des caractéristiques des générateurs, par exemple un refroidisseur à absorption par rapport à un refroidisseur centrifuge | Feste Reihenfolge nur auf der Grundlage von Lasten: z. B. abhängig von den Eigenschaften des Generators wie Absorptionskälteanlage vs. Zentrifugalkälteanlage
overview of services | 511 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Remontée centralisée ou déportée d'indicateurs temps réel de performance (température, sous-comptage) | Zentrale oder ferngesteuerte Berichterstattung über aktuelle Leistungskennzahlen (z. B. Temperaturen, Submetering-Energieverbrauch)
overview of services | 512 | Scheduled operation of cooling system | Scheduled operation of cooling system | Programmation des plages de fonctionnement du système de refroidissement | Planmäßiger Betrieb des Kühlsystems
overview of services | 513 | Clock control | Clock control | Régulation programmée | Uhrenkontrolle
overview of services | 514 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | Programmation des heures de mise en marche/arrêt : fournit en continu un débit d'air pour une charge maximale pour toutes les pièces au cours d'un temps d'occupation nominal | Ein-Aus-Zeitsteuerung: Kontinuierliche Zufuhr des Luftstroms für eine maximale Belüftung aller Räume während der Nennbelegungszeit
overview of services | 515 | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on sensors in air exhaust | Modulation ou bipasse de la récupération de chaleur selon des données venant de capteurs dans l'air extrait | Anpassung oder Umgehung der Wärmerückgewinnung anhand von Sensoren in der Abluft
overview of services | 516 | Constant setpoint: A control loop enables to control the supply air_x000D_ temperature, the setpoint is constant and can only be modified by a manual_x000D_ action | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action | Point de consigne constant : une boucle de régulation permet de réguler la température de l'air introduit, le point de consigne est constant et ne peut être modifié que par une action manuelle | Konstanter Sollwert: Ein Regelkreis ermöglicht die Regelung der Zulufttemperatur, der Sollwert ist konstant und kann nur manuel geändert werden
overview of services | 517 | Night cooling | Night cooling | Refroidissement nocturne | Kühlung in der Nacht
overview of services | 518 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Capteurs de qualité de l'air (ex. CO2) et suivi autonome en temps réel | Luftqualitätssensoren (z. B. CO2) und autonome Echtzeitüberwachung
overview of services | 519 | Manual on/off switch + additional sweeping extinction signal | Manual on/off switch + additional sweeping extinction signal | Interrupteur manuel de mise en marche/arrêt + signal supplémentaire d'extinction | Manueller Ein/Aus-Schalter + zusätzliches Tonsignal
overview of services | 520 | Manual (per room / zone) | Manual (per room / zone) | Manuelle (par pièce ou zone) | Manuell (pro Raum/Zone)
overview of services | 521 | Motorized operation with manual control | Motorized operation with manual control | Motorisation des protections solaires commandée par interrupteur | Motorbetrieb mit manueller Steuerung
overview of services | 522 | Open/closed detection to shut down heating or cooling systems | Open/closed detection to shut down heating or cooling systems | Capteur d'ouverture/fermeture pour extinction des systèmes de chauffage ou refroidissement | Erkennung von offenem/geschlossenem Zustand zum Abschalten von Heiz- oder Kühlsystemen
overview of services | 523 | Position of each product & fault detection | Position of each product & fault detection | Position de chaque produit et détection des défauts | Position der einzelnen Produkte und Fehlererkennung
overview of services | 524 | Current generation data available | Current generation data available | Données sur la production actuelle disponibles | Aktuelle Erzeugungsdaten verfügbar
overview of services | 525 | On site storage of electricity (e.g. electric battery) | On site storage of electricity (e.g. electric battery) | Stockage d'électricité sur place (par exemple batterie) | Speicherung von Strom vor Ort (z. B. elektrische Batterie)
overview of services | 526 | Scheduling electricity consumption (plug loads, white goods, etc.) | Scheduling electricity consumption (plug loads, white goods, etc.) | Programmation temporelle (prises, électroménager, etc.) | Planung des Stromverbrauchs (Steckdosenlasten, Haushaltsgeräte, usw.)
overview of services | 527 | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | Fonctionnement de la cogénération en fonction de la disponibilité intermittente des sources d'énergie renouvelables | Steuerung der KWK-Laufzeit unter dem Einfluss der schwankenden Verfügbarkeit von EE; Überproduktion wird ins Netz eingespeist
overview of services | 528 | Automated management of (building-level) electricity consumption based on grid signals | Automated management of (building-level) electricity consumption based on grid signals | Gestion automatisée de la consommation d'électricité (au niveau du bâtiment) en fonction des signaux du réseau | Automatisiertes Management des Stromverbrauchs (auf Gebäudeebene) auf der Grundlage von Netzsignalen
overview of services | 529 | Current state of charge (SOC) data available | Current state of charge (SOC) data available | Information sur l'état de charge (SOC) disponible | Aktuelle Ladungszustandsdaten (SOC) verfügbar
overview of services | 530 | reporting on current electricity consumption on building level | reporting on current electricity consumption on building level | Retour d'informations sur la consommation actuelle d'électricité du bâtiment | Berichterstattung über den aktuellen Stromverbrauch auf Gebäudeebene
overview of services | 531 | ducting (or simple power plug) available | ducting (or simple power plug) available | Borne de recharge ou simple prise électrique disponible | Elektroinstallation (oder einfacher Netzstecker) vorhanden
overview of services | 532 | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | Contrôle unidirectionnel de la charge (ex. intégrant heure souhaitée de départ et optimisation en fonction des ordres reçus de la part du réseau) | 1-Weg-gesteuertes Laden (z.B. mit gewünschter Abfahrtszeit und Netzsignalen zur Optimierung)
overview of services | 533 | Reporting information on EV charging status to occupant | Reporting information on EV charging status to occupant | Communication d'informations sur l'état de charge des véhicules électriques à l'occupant | Meldung von Informationen über den Ladestatus des Fahrzeugs an den Nutzer
overview of services | 534 | Runtime setting of heating and cooling plants following a predefined time schedule | Runtime setting of heating and cooling plants following a predefined time schedule | Configuration des systèmes de production de chaud et de froid en fonction d'un calendrier horaire prédéfini | Laufzeiteinstellung von Heiz- und Kühlanlagen nach einem vordefinierten Zeitplan
overview of services | 535 | With central indication of detected faults and alarms for at least 2 relevant TBS | With central indication of detected faults and alarms for at least 2 relevant TBS | Avec indication centralisée de détection des fautes et alarmes pour au moins 2 systèmes techniques du bâtiment pertinents | Mit zentraler Anzeige von erkannten Fehlern und Alarmen für mindestens 2 relevante TBS
overview of services | 536 | Occupancy detection for individual functions, e.g. lighting | Occupancy detection for individual functions, e.g. lighting | Détection d'occupation pour des fonctions individuelles (par exemple l'éclairage) | Belegungserkennung für einzelne Funktionen, z. B. Beleuchtung
overview of services | 537 | Central or remote reporting of realtime energy use per energy carrier | Central or remote reporting of realtime energy use per energy carrier | Remontée centralisée ou déportée d'indicateurs temps réel d'utilisation d'énergie par vecteur énergétique | Zentrale oder Remote-Berichterstattung über den Echtzeit-Energieverbrauch pro Energieträger
overview of services | 538 | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Gestion de la demande possible pour certains systèmes techniques du bâtiment (sans coordination entre domaines) | Bedarfsabhängige Regelung für (einige) einzelne TBS möglich, aber nicht über verschiedene Bereiche hinweg koordiniert
overview of services | 539 | Reporting information on current DSM status, including managed energy flows | Reporting information on current DSM status, including managed energy flows | Remontée d'informations sur le statut actuel de gestion de la demande, intégrant les flux d'énergie concernés | Berichterstattung über den aktuellen DSM-Status, einschließlich der verwalteten Energieflüsse
overview of services | 540 | DSM control without the possibility to override this control by the building user (occupant or facility manager) | DSM control without the possibility to override this control by the building user (occupant or facility manager) | Contrôle de gestion de la demande sans possibilité pour l'utilisateur (occupant ou gestionnaire) de le préempter | DSM-Steuerung ohne die Möglichkeit, diese Steuerung durch den Gebäudenutzer (Bewohner oder Facility Manager) außer Kraft zu setzen
overview of services | 541 | Single platform that allows manual control of multiple TBS | Single platform that allows manual control of multiple TBS | Plateforme unique permettant le contrôle manuel de plusieurs systèmes techniques du bâtiment | Eine einzige Plattform, die die manuelle Steuerung mehrerer TBS ermöglicht
overview of services | 542 | Functionality level 2 | Functionality level 2 | Niveau de fonctionnalité 2 | Funktionalitätsstufe 2
overview of services | 543 | 0
overview of services | 544 | 0
overview of services | 545 | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control (e.g. thermostatic valves, or electronic controller) | Régulation individuelle par pièce (par exemple robinets thermostatiques, ou thermostat électronique) | Einzelraumregelung (z.B. Thermostatventile, oder elektronische Regler)
overview of services | 546 | Advanced central automatic control | Advanced central automatic control | Régulation centrale automatique évoluée | Erweiterte zentrale automatische Steuerung
overview of services | 547 | Demand based control | Demand based control | Régulation basée sur les besoins | Bedarfsorientierte Steuerung
overview of services | 548 | Multi-Stage control | Multi-Stage control | Commande multi-vitesse | Mehrstufige Steuerung
overview of services | 549 | Load prediction based storage operation | Load prediction based storage operation | Stockage géré selon des prévisions de consommation | Auf Lastvorhersage basierender Speicherbetrieb
overview of services | 550 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | Régulation de température variable en fonction de la charge : par exemple en fonction du point de consigne de température d'eau distribuée | Variable Temperaturregelung in Abhängigkeit von der Last (z.B. in Abhängigkeit vom Sollwert der Vorlauftemperatur)
overview of services | 551 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Régulation variable de la capacité des générateurs de chaleur en fonction de la charge ou de la demande (par exemple contournement des gaz chauds, régulation de fréquence de l'onduleur) | Variable Steuerung der Wärmeerzeugerleistung in Abhängigkeit von der Last oder dem Bedarf (z. B. Heißgas-Bypass, Frequenzregelung des Wechselrichters)
overview of services | 552 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Régulation basée sur une liste dynamique des priorités basée sur le rendement et les capacités actuelles des générateurs : par exemple : chaleur solaire, chaleur géothermique, installation de cogénération, combustibles fossiles | Steuerung nach dynamischer Prioritätenliste (auf der Grundlage der aktuellen Energieeffizienz, der Kohlenstoffemissionen und der Kapazität der Erzeuger, z. B. Solarenergie, Erdwärme, Kraft-Wärme-Kopplungsanlagen, fossile Brennstoffe)
overview of services | 553 | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of current performance KPIs and historical data | Remontée centralisée ou déportée d'indicateurs temps réel de performance et des données historisées | Zentrale oder dezentrale Berichterstattung über aktuelle Leistungskennzahlen und historische Daten
overview of services | 554 | Self-learning optimal control of heating system | Self-learning optimal control of heating system | Pilotage par auto-apprentissage du système de chauffage | Selbstlernende optimale Steuerung eines Heizungssystems
overview of services | 555 | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Commande automatique de mise en marche/arrêt et déclenchement du temps de charge et gestion de stockage avec plusieurs capteurs | Automatisches Ein- und Ausschalten, zeitgesteuertes Laden und Multi-Sensor-Speicherverwaltung
overview of services | 556 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | Commande automatique de mise en marche/arrêt, déclenchement du temps de charge et régulation de la température d'alimentation selon les besoins ou gestion de stockage avec plusieurs capteurs | Automatisches Ein- und Ausschalten, zeitgesteuertes Aufladen und bedarfsgerechte Vorlauftemperaturregelung oder Multi-Sensor-Speicherverwaltung
overview of services | 557 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Commande automatique de la charge de stockage d’énergie solaire (Priorité 1) et charge de stockage supplémentaire (priorité 2) et régulation de la température d'alimentation selon les besoins ou gestion de stockage avec plusieurs capteurs | Automatische Steuerung von Solarspeicherladung (Prio. 1) und Speicherergänzungsladung und bedarfsgerechte Versorgung oder Multisensor-Speicher-Management
overview of services | 558 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Régulation basée sur une liste dynamique des priorités basée sur le rendement et les capacités actuelles des générateurs : par exemple : chaleur solaire, chaleur géothermique, installation de cogénération, combustibles fossiles | Steuerung nach dynamischer Prioritätenliste (auf der Grundlage der aktuellen Energieeffizienz, der Kohlenstoffemissionen und der Kapazität der Erzeuger, z. B. Solarenergie, Erdwärme, Kraft-Wärme-Kopplungsanlagen, fossile Brennstoffe)
overview of services | 559 | Actual values and historical data | Actual values and historical data | Indication des valeurs réelles et données historisées | Tatsächliche Werte und historische Daten
overview of services | 560 | Individual room control | Individual room control | Régulation individuelle par pièce | Einzelraumregelung
overview of services | 561 | Advanced central automatic control | Advanced central automatic control | Régulation centrale automatique évoluée | Erweiterte zentrale automatische Steuerung
overview of services | 562 | Demand based control | Demand based control | Régulation basée sur les besoins | Bedarfsabhängige Regelung
overview of services | 563 | Multi-Stage control | Multi-Stage control | Commande multi-vitesse | Mehrstufige Steuerung
overview of services | 564 | Total interlock (control system ensures no simultaneous heating and cooling can take place) | Total interlock (control system ensures no simultaneous heating and cooling can take place) | Asservissement total : La fonction de régulation permet de garantir qu'il n'y aura aucun chauffage et refroidissement simultanés | Vollständige Verriegelung (das Kontrollsystem stellt sicher, dass nicht gleichzeitig geheizt und gekühlt werden kann)
overview of services | 565 | Load prediction based storage operation | Load prediction based storage operation | Stockage géré selon des prévisions de consommation | Auf Lastvorhersage basierender Speicherbetrieb
overview of services | 566 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Régulation variable de la capacité des générateurs de froid en fonction de la charge ou de la demande (par exemple contournement des gaz chauds, régulation de fréquence de l'onduleur) | Variable Steuerung der Kälteerzeugungsleistung in Abhängigkeit von der Last oder dem Bedarf (z. B. Heißgas-Bypass, Frequenzregelung des Wechselrichters)
overview of services | 567 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Priorités dynamiques basées sur le rendement et les caractéristiques des générateurs (par exemple, possibilité de refroidissement naturel) | Dynamische Prioritäten auf der Grundlage des Wirkungsgrads und der Eigenschaften des Generators (z. B. Verfügbarkeit von freier (Passiv-)Kühlung)
overview of services | 568 | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of current performance KPIs and historical data | Remontée centralisée ou déportée d'indicateurs temps réel de performance et des données historisées | Zentrale oder dezentrale Berichterstattung über aktuelle Leistungskennzahlen und historische Daten
overview of services | 569 | Self-learning optimal control of cooling system | Self-learning optimal control of cooling system | Pilotage par auto-apprentissage du système de refroidissement | Selbstlernende optimale Steuerung eines Kühlsystems
overview of services | 570 | Occupancy detection control | Occupancy detection control | Régulation basée sur l’occupation | Steuerung der Anwesenheitserkennung
overview of services | 571 | Multi-stage control: To reduce the auxiliary energy demand of the fan | Multi-stage control: To reduce the auxiliary energy demand of the fan | Régulation multi-niveau : pour diminuer les besoins en énergie auxiliaire du ventilateur | Mehrstufige Steuerung: Zur Reduzierung des Hilfsenergiebedarfs des Ventilators
overview of services | 572 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | Modulation ou bipasse de la récupération de chaleur selon des données venant de capteurs dans l'air extrait ou du contrôle prédictif | Modulierung oder Umgehung der Wärmerückgewinnung auf der Grundlage mehrerer Raumtemperatursensoren oder vorausschauender Steuerung
overview of services | 573 | Variable set point with outdoor temperature compensation | Variable set point with outdoor temperature compensation | Point de consigne variable avec compensation de la température extérieure | Variabler Sollwert mit Außentemperaturkompensation
overview of services | 574 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical_x000D_ cooling | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling | Refroidissement naturel : les quantités d'air sont modulées au cours de toutes les périodes afin de réduire le plus possible la quantité de refroidissement mécanique. | Freie Kühlung: modulierte Luftströme während aller Zeiträume, um die mechanische Kühlung zu minimieren
overview of services | 575 | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants | Suivi en temps réel et données historisées sur la qualité de l'air intérieur mise à disposition des occupants | Echtzeit-Überwachung und historische Informationen über IAQ für die Bewohner verfügbar
overview of services | 576 | Automatic detection (auto on / dimmed or auto off) | Automatic detection (auto on / dimmed or auto off) | Détection automatique. Mise en marche automatique/Arrêt avec modulation par variateur | Automatische Erkennung (auto on / dimmed oder auto off)
overview of services | 577 | Automatic switching | Automatic switching | Commutation automatique | Automatische Umschaltung
overview of services | 578 | Motorized operation with automatic control based on sensor data | Motorized operation with automatic control based on sensor data | Motorisation des protections solaires avec pilotage automatique en fonction de données mesurées | Motorisierter Betrieb mit automatischer Steuerung auf der Grundlage von Sensordaten
overview of services | 579 | Level 1 + Automised mechanical window opening based on room sensor data | Level 1 + Automised mechanical window opening based on room sensor data | Niveau 1 + ouverture automatique des fenêtres en fonction de données mesurées par des capteurs dans la pièce | Stufe 1 + Automatisierte mechanische Fensteröffnung auf der Grundlage von Raumsensordaten
overview of services | 580 | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection & predictive maintenance | Position de chaque produit, détection des défauts et maintenance prédictive | Position der einzelnen Produkte, Fehlererkennung und vorausschauende Wartung
overview of services | 581 | Actual values and historical data | Actual values and historical data | Valeurs réelles et données historisées | Tatsächliche Werte und historische Daten
overview of services | 582 | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | Stockage d'énergie sur site (par exemple, batterie ou stockage thermique) avec régulation en fonction d'ordres reçus de la part du réseau | Vor-Ort-Energiespeicherung (z. B. elektrische Batterie oder thermische Speicherung) mit Steuerung auf der Grundlage von Netzsignalen
overview of services | 583 | Automated management of local electricity consumption based on current renewable energy availability | Automated management of local electricity consumption based on current renewable energy availability | Gestion automatisée de la consommation d'électricité produite localement en fonction de la disponibilité temps-réel des énergies renouvelables | Automatisiertes Management des lokalen Stromverbrauchs auf der Grundlage der aktuellen Verfügbarkeit erneuerbarer Energien
overview of services | 584 | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | Fonctionnement de la cogénération en fonction de la disponibilité intermittente des sources d'énergie renouvelables et en fonction d'ordres reçus de la part du réseau; alimentation dynamique et contrôle optimisé pour favoriser l'autoconsommation des renouvelables | Steuerung der KWK-Laufzeit in Abhängigkeit von der schwankenden Verfügbarkeit erneuerbarer Energien und Netzsignalen; dynamische Lade- und Laufzeitsteuerung zur Optimierung des Eigenverbrauchs erneuerbarer Energien
overview of services | 585 | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Gestion automatisée de la consommation d'électricité du bâtiment et de la fourniture d'électricité aux bâtiments voisins (micro-réseau) ou au réseau | Automatisiertes Management des Stromverbrauchs (auf Gebäudeebene) und der Stromversorgung benachbarter Gebäude (Microgrid) oder des Stromnetzes
overview of services | 586 | Actual values and historical data | Actual values and historical data | Valeurs réelles et données historisées | Tatsächliche Werte und historische Daten
overview of services | 587 | real-time feedback or benchmarking on building level | real-time feedback or benchmarking on building level | Remontée d'informations en temps réel ou analyse comparative au niveau du bâtiment | Echtzeit-Feedback oder Benchmarking auf Gebäudeebene
overview of services | 588 | 0-9% of parking spaces has recharging points | 0-9% of parking spaces has recharging points | Entre 0% et 9% des places de parking ont une borne de recharge | 0-9% der Parkplätze sind mit Ladestationen ausgestattet
overview of services | 589 | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | Charge bidirectionnelle (ex. intégrant heure souhaitée de départ et optimisation en fonction des ordres reçus de la part du réseau) | 2-Wege-gesteuertes Laden (z.B. mit gewünschter Abfahrtszeit und Netzsignalen zur Optimierung)
overview of services | 590 | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | Communication d'informations sur l'état de charge des véhicules électriques à l'occupant ET identification et autorisation automatiques du conducteur à la station de recharge (conforme ISO 15118) | Meldung von Informationen über den Ladestatus des E-Fahrzeugs an den Fahrzeuginsassen UND automatische Identifizierung und Autorisierung des Fahrers an der Ladestation (ISO 15118-konform)
overview of services | 591 | Heating and cooling plant on/off control based on building loads | Heating and cooling plant on/off control based on building loads | Mise en marche / arrêt des systèmes de chauffage et refroidissement en fonction de la demande du bâtiment | Ein- und Ausschalten von Heiz- und Kühlanlagen in Abhängigkeit von der Gebäudelast
overview of services | 592 | With central indication of detected faults and alarms for all relevant TBS | With central indication of detected faults and alarms for all relevant TBS | Avec indication centralisée de détection des fautes et alarmes pour tous les systèmes techniques du bâtiment pertinents | Mit zentraler Anzeige von erkannten Fehlern und Alarmen für alle relevanten TBS
overview of services | 593 | Centralised occupant detection which feeds in to several TBS such as lighting and heating | Centralised occupant detection which feeds in to several TBS such as lighting and heating | Détection d'occupation centralisée qui alimentent plusieurs systèmes techniques du bâtiment tels que l'éclairage et le chauffage | Zentralisierte Personenerkennung, die mehrere TBS wie Beleuchtung und Heizung steuert
overview of services | 594 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | Remontée centralisée ou déportée d'indicateurs temps réel d'utilisation d'énergie par vecteur énergétique, combinant les systèmes techniques du bâtiment pour au moins 2 domaines en une seule interface | Zentrale oder ferngesteuerte Meldung des Echtzeit-Energieverbrauchs pro Energieträger, wobei die TBS von mindestens 2 Bereiche in einer Schnittstelle kombiniert werden
overview of services | 595 | Coordinated demand side management of multiple TBS | Coordinated demand side management of multiple TBS | Gestion coordonnée de la demande pour plusieurs systèmes techniques du bâtiment | Koordinierte Nachfragesteuerung für mehrere TBS
overview of services | 596 | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | Remontée d'information sur le statut actuel, passé et prévisionnel de la gestion de la demande, intégrant les flux d'énergie concernés | Berichterstattung über den aktuellen und prognostizierten DSM-Status, einschließlich der verwalteten Energieflüsse
overview of services | 597 | Manual override and reactivation of DSM control by the building user | Manual override and reactivation of DSM control by the building user | Préemption manuelle et réactivation du contrôle de gestion de la demande par l'utilisateur | Manuelle Überbrückung und Reaktivierung der DSM-Steuerung durch den Gebäudenutzer
overview of services | 598 | Single platform that allows automated control & coordination between TBS | Single platform that allows automated control & coordination between TBS | Plateforme unique permettant le contrôle automatique et la coordination entre tous les systèmes techniques du bâtiment | Eine einzige Plattform, die eine automatische Kontrolle und Koordination zwischen TBS
overview of services | 599 | Functionality level 3 | Functionality level 3 | Niveau de fonctionnalité 3 | Funktionalitätsstufe 3
overview of services | 600 | 0
overview of services | 601 | 0
overview of services | 602 | Individual room control with communication between controllers and to BACS | Individual room control with communication between controllers and to BACS | Régulation individuelle par pièce avec communication entre les régulateurs et le système de GTB | Einzelraumregelung mit Kommunikation zwischen Reglern und zu BACS
overview of services | 603 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Régulation centrale automatique évoluée avec fonctionnement par intermittence et/ou commande à rétroaction de température ambiante | Fortgeschrittene zentrale automatische Steuerung mit intermittierendem Betrieb und/oder Rückführung der Raumtemperatur
overview of services | 604 | 0
overview of services | 605 | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (pump unit (internal) estimations) | Commande des pompes à vitesse variable (régulation intégrée aux pompes) | Pumpensteuerung mit variabler Drehzahl (Schätzungen des Pumpenaggregats (intern))
overview of services | 606 | Heat storage capable of flexible control through grid signals (e.g. DSM) | Heat storage capable of flexible control through grid signals (e.g. DSM) | Pilotage possible selon les ordres reçus du réseau (par exemple, effacements) | Wärmespeicher, die durch Netzsignale flexibel gesteuert werden können (z. B. DSM)
overview of services | 607 | 0
overview of services | 608 | Variable control of heat generator capacity depending on the load AND external signals from grid | Variable control of heat generator capacity depending on the load AND external signals from grid | Régulation variable de la capacité des générateurs de chaleur en fonction de la charge ou de la demande ET selon les ordres reçus du réseau | Variable Steuerung der Wärmeerzeugerleistung in Abhängigkeit von der Last UND externen Signalen aus dem Netz
overview of services | 609 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Régulation selon priorités calculées dynamiquement en fonction de critères temps réel et de prévisions (efficacité énergétique, émissions de CO2, capacité des générateurs) | Steuerung nach dynamischer Prioritätenliste (basierend auf aktueller UND prognostizierter Last, Energieeffizienz, Kohlendioxidemissionen und Kapazität der Erzeuger)
overview of services | 610 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Remontée centralisée ou déportée d'indicateurs temps réel incluant prévisions et comparaisons | Zentrale oder dezentrale Berichterstattung über die Leistungsbewertung einschließlich Prognosen und/oder Benchmarking
overview of services | 611 | Heating system capable of flexible control through grid signals (e.g. DSM) | Heating system capable of flexible control through grid signals (e.g. DSM) | Pilotage du système de chauffage en fonction d'ordres reçus de la part du réseau | Heizsystem mit flexibler Steuerung durch Netzsignale (z. B. DSM)
overview of services | 612 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | Commande du système de chauffage en fonction de la production locale d'énergie renouvelable ou d'ordres reçus de la part du réseau (effacement) | Automatische Ladesteuerung basierend auf der lokalen Verfügbarkeit von erneuerbaren Energien oder Informationen aus dem Stromnetz (DR, DSM)
overview of services | 613 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | Système de production d'eau chaude piloté par des informations extérieures (par exemple, de la part du réseau de chaleur) | Trinkwarmwasserbereitungsanlage mit automatischer Ladesteuerung auf der Grundlage externer Signale (z. B. vom Fernwärmenetz)
overview of services | 614 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | Commande automatique de la charge de stockage d’énergie solaire (Priorité 1) et charge de stockage supplémentaire (priorité 2)et régulation de la température d'alimentation selon les besoins ou gestion de stockage avec plusieurs capteurs | Automatische Regelung von Solarspeicherladung (Prio. 1) und Speicherergänzungsladung, bedarfsgerechte Vor- und Rücklauftemperaturregelung und Multi-Sensor-Speicher-Management
overview of services | 615 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Régulation selon priorités calculées dynamiquement en fonction de critères temps réel et de prévisions (efficacité énergétique, émissions de CO2, capacité des générateurs) | Steuerung nach dynamischer Prioritätenliste (basierend auf aktueller UND prognostizierter Last, Energieeffizienz, Kohlendioxidemissionen und Kapazität der Erzeuger)
overview of services | 616 | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking | Evaluation de la performance incluant prévisions et/ou comparaisons | Leistungsbewertung einschließlich Prognosen und/oder Benchmarking
overview of services | 617 | Individual room control with communication between controllers and to BACS | Individual room control with communication between controllers and to BACS | Régulation individuelle par pièce avec communication entre les régulateurs et le système de GTB | Einzelraumregelung mit Kommunikation zwischen Reglern und zu BACS
overview of services | 618 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Régulation centrale automatique évoluée avec fonctionnement par intermittence et/ou commande à rétroaction de température ambiante | Fortgeschrittene zentrale automatische Steuerung mit intermittierendem Betrieb und/oder Rückführung der Raumtemperatur
overview of services | 619 | 0
overview of services | 620 | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (pump unit (internal) estimations) | Commande des pompes à vitesse variable (régulation intégrée aux pompes) | Pumpensteuerung mit variabler Drehzahl (Schätzungen des Pumpenaggregats (intern))
overview of services | 621 | 0
overview of services | 622 | Cold storage capable of flexible control through grid signals (e.g. DSM) | Cold storage capable of flexible control through grid signals (e.g. DSM) | Pilotage possible selon les ordres reçus du réseau (par exemple, effacements) | Kältespeicher, die durch Netzsignale flexibel gesteuert werden können (z. B. DSM)
overview of services | 623 | Variable control of cooling production capacity depending on the load AND external signals from grid | Variable control of cooling production capacity depending on the load AND external signals from grid | Régulation variable de la capacité des générateurs de froid en fonction de la charge ou de la demande ET selon les ordres reçus du réseau | Variable Steuerung der Kühlleistung in Abhängigkeit von der Last UND externen Signalen aus dem Netz
overview of services | 624 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Ordre de priorité basé sur les prédictions de charges : l'ordre est par exemple basé sur le coefficient de performance (COP) et la puissance disponible d'un appareil, ainsi que sur la puissance nécessaire prévue | Auf Lastvorhersage basierende Sequenzierung: Die Sequenzierung basiert z. B. auf dem COP und der verfügbaren Leistung eines Geräts und der vorhergesagten erforderlichen Leistung
overview of services | 625 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Remontée centralisée ou déportée d'indicateurs temps réel incluant prévisions et comparaisons | Zentrale oder dezentrale Berichterstattung über die Leistungsbewertung einschließlich Prognosen und/oder Benchmarking
overview of services | 626 | Cooling system capable of flexible control through grid signals (e.g. DSM) | Cooling system capable of flexible control through grid signals (e.g. DSM) | Pilotage du système de refroidissement en fonction d'ordres reçus de la part du réseau | Kühlsystem mit flexibler Steuerung durch Netzsignale (z. B. DSM)
overview of services | 627 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Régulation centralisée en fonction de données venant de capteurs de qualité de l'air (CO2, COV, humidité...) | Zentrale Bedarfssteuerung auf der Grundlage von Luftqualitätssensoren (CO2, VOC, Feuchtigkeit, ...)
overview of services | 628 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Régulation automatique du débit ou de la pression sans réinitialisation de la pression : charge en fonction des alimentations du débit d'air selon les besoins pour toutes les pièces communicantes | Automatische Volumenstrom- oder Druckregelung ohne Druckrückstellung: Lastabhängige Versorgung des Luftstroms für den Bedarf aller angeschlossenen Räume.
overview of services | 629 | 0
overview of services | 630 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | Point de consigne variable avec compensation en fonction de la charge : une boucle de régulation permet de réguler la température de l'air introduit. Le point de consigne est défini comme une fonction des charges dans la pièce | Variabler Sollwert mit lastabhängiger Kompensation. Ein Regelkreis ermöglicht die Regelung der Zulufttemperatur. Der Sollwert wird in Abhängigkeit von den Lasten im Raum definiert
overview of services | 631 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | Régulation directe H,x : les quantités d'air extérieur et d'air de recirculation sont modulées au cours de toutes les périodes afin de réduire le plus possible la quantité de refroidissement mécanique. Un calcul est réalisé sur la base des températures et de l'humidité (enthalpie) | H,x-gesteuerte Regelung: Die Menge der Außenluft und der Umluft wird während aller Zeiträume moduliert, um die Menge der mechanischen Kühlung zu minimieren. Die Berechnung erfolgt auf der Grundlage von Temperaturen und Feuchtigkeit
overview of services | 632 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | Suivi en temps réel et données historisées sur la qualité de l'air intérieur mise à disposition des occupants + alarme sur les besoins de maintenance ou les actions des occupants (ex: ouverture de fenêtre) | Echtzeit-Überwachung und historische IAQ-Informationen, die den Bewohnern zur Verfügung stehen + Warnung bei Wartungsbedarf oder Bewohneraktionen (z. B. Öffnen von Fenstern)
overview of services | 633 | Automatic detection (manual on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) | Détection automatique: Mise en marche manuelle/Mise en marche partiellement automatique/Arrêt du variateur | Automatische Erkennung (manuell ein/gedimmt oder automatisch aus)
overview of services | 634 | Automatic dimming | Automatic dimming | Modulation automatique | Automatisches Dimmen
overview of services | 635 | Combined light/blind/HVAC control | Combined light/blind/HVAC control | Régulation combinée de l'éclairage, des protections solaires et du système CVC | Kombinierte Licht-/Jalousie-/HLK-Steuerung
overview of services | 636 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | Niveau 2 + coordination centralisée des ouvrants (ex: pour contrôler le refroidissement naturel nocturne) | Stufe 2 + Zentrale Koordinierung von bedienbaren Fenstern, z. B. zur Steuerung der freien natürlichen Nachtauskühlung
overview of services | 637 | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position de chaque produit, détection des défauts, maintenance prédictive et données temps-réel (vent, luminosité, température) | Position der einzelnen Produkte, Fehlererkennung, vorausschauende Wartung, Sensordaten in Echtzeit (Wind, Lux, Temperatur...)
overview of services | 638 | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking | Evaluation de la performance incluant prévisions et/ou comparaisons | Leistungsbewertung einschließlich Prognosen und/oder Benchmarking
overview of services | 639 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | Stockage d'énergie sur site (par exemple, batterie ou stockage thermique) avec optimisation de l'utilisation de l'électricité produite localement | Energiespeicherung vor Ort (z. B. elektrische Batterie oder thermische Speicherung) mit Steuerung zur Optimierung der Nutzung des lokalen erzeugten Stroms
overview of services | 640 | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | Gestion automatisée de la consommation d'électricité produite localement en fonction des prévisions de besoins d'énergie et de la disponibilité temps-réel des énergies renouvelables | Automatisiertes Management des lokalen Stromverbrauchs auf der Grundlage des aktuellen und prognostizierten Energiebedarfs und der Verfügbarkeit erneuerbarer Energie
overview of services | 641 | 0
overview of services | 642 | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | Gestion automatisée de la consommation d'électricité du bâtiment et de la fourniture d'électricité, avec la possibilité de fonctionnement partiel hors-réseau (mode îlotage) | Automatisiertes Management von Stromverbrauch und -versorgung (auf Gebäudeebene) mit der Möglichkeit, in begrenztem Umfang weiterhin netzunabhängig zu arbeiten (Inselbetrieb)
overview of services | 643 | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking | Evaluation de la performance incluant prévisions et/ou comparaisons | Leistungsbewertung einschließlich Prognosen und/oder Benchmarking
overview of services | 644 | real-time feedback or benchmarking on appliance level | real-time feedback or benchmarking on appliance level | Retour d'information en temps réel ou analyse comparative au niveau des appareils | Echtzeit-Feedback oder Benchmarking auf Geräteebene
overview of services | 645 | 10-50% or parking spaces has recharging point | 10-50% or parking spaces has recharging point | Entre 10% et 50% des places de parking ont une borne de recharge | 10-50% der Parkplätze haben eine Aufladestation
overview of services | 646 | 0
overview of services | 647 | 0
overview of services | 648 | Heating and cooling plant on/off control based on predictive control or grid signals | Heating and cooling plant on/off control based on predictive control or grid signals | Mise en marche / arrêt des systèmes de chauffage et refroidissement en fonction de la demande du bâtiment ou d'ordres reçus de la part du réseau | Ein- und Ausschalten von Heiz- und Kühlanlagen auf der Grundlage einer vorausschauenden Steuerung oder von Netzsignalen
overview of services | 649 | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | Avec indication centralisée de détection des fautes et alarmes pour tous les systèmes techniques du bâtiment pertinents, intégrant des fonctions de diagnostic | Mit zentraler Anzeige von erkannten Fehlern und Alarmen für alle relevanten TBS, einschließlich Diagnosefunktionen
overview of services | 650 | 0
overview of services | 651 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | Remontée centralisée ou déportée d'indicateurs temps réel d'utilisation d'énergie par vecteur énergétique, combinant les systèmes techniques du bâtiment pour tous les domaines principaux en une seule interface | Zentrale oder ferngesteuerte Berichterstattung über den Echtzeit-Energieverbrauch pro Energieträger, die die TBS aller Hauptbereiche in einer Schnittstelle zusammenfasst
overview of services | 652 | 0
overview of services | 653 | 0
overview of services | 654 | Scheduled override of DSM control (and reactivation) by the building user | Scheduled override of DSM control (and reactivation) by the building user | Préemption (et réactivation) programmée du contrôle de gestion de la demande par l'utilisateur | Planmäßige Aufhebung der DSM-Steuerung (und Reaktivierung) durch den Gebäudenutzer
overview of services | 655 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Plateforme unique permettant le contrôle automatique et la coordination entre les systèmes techniques du bâtiment + optimisation des flux d'énergie en fonction de l'occupation, de la météo et des ordres reçus de la part du réseau | Eine einzige Plattform, die eine automatische Steuerung und Koordinierung zwischen den TBS sowie eine Optimierung des Energieflusses auf der Grundlage von Belegung, Wetter und Netzsignalen ermöglicht
overview of services | 656 | Functionality level 4 | Functionality level 4 | Niveau de fonctionnalité 4 | Funktionalitätsstufe 4
overview of services | 657 | 0
overview of services | 658 | 0
overview of services | 659 | Individual room control with communication and occupancy detection | Individual room control with communication and occupancy detection | Régulation individuelle par pièce avec communication et détection d’occupation | Einzelraumregelung mit Kommunikation und Anwesenheitserkennung
overview of services | 660 | 0
overview of services | 661 | 0
overview of services | 662 | Variable speed pump control (external demand signal) | Variable speed pump control (external demand signal) | Commande des pompes à vitesse variable (signal de commande externe) | Pumpensteuerung mit variabler Drehzahl (externes Bedarfssignal)
overview of services | 663 | 0
overview of services | 664 | 0
overview of services | 665 | 0
overview of services | 666 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Régulation selon priorités calculées dynamiquement en fonction de critères temps réel et de prévisions (efficacité énergétique, émissions de CO2, capacité des générateurs) ET selon les ordres reçus du réseau | Steuerung nach dynamischer Prioritätenliste (basierend auf aktueller UND prognostizierter Last, Energieeffizienz, Kohlenstoffemissionen, Kapazität der Erzeuger UND externen Signalen aus dem Netz)
overview of services | 667 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Remontée centralisée ou déportée d'indicateurs incluant prévisions, comparaisons, identification de dérives et gestion prévisionnelle | Zentrale oder ferngesteuerte Berichterstattung über die Leistungsbewertung, einschließlich Prognosen und/oder Benchmarking; einschließlich vorausschauendes Management und Fehlererkennung
overview of services | 668 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | Pilotage optimisé du système de chauffage selon des prévisions locales et des ordres de la part du réseau | Optimierte Steuerung der Heizungsanlage auf der Grundlage lokaler Vorhersagen und Netzsignale (z. B. durch modellprädiktive Steuerung)
overview of services | 669 | 0
overview of services | 670 | 0
overview of services | 671 | 0
overview of services | 672 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Régulation selon priorités calculées dynamiquement en fonction de critères temps réel et de prévisions (efficacité énergétique, émissions de CO2, capacité des générateurs) et des ordres de la part du réseau | Steuerung nach dynamischer Prioritätenliste (basierend auf aktueller UND prognostizierter Last, Energieeffizienz, Kohlenstoffemissionen, Kapazität der Erzeuger UND externen Signalen aus dem Netz)
overview of services | 673 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Evaluation de performance incluant prévisions et/ou comparaisons, identification de dérives et gestion prévisionnelle | Leistungsbewertung, einschließlich Vorhersage und/oder Benchmarking; einschließlich vorausschauendes Management und Fehlererkennung
overview of services | 674 | Individual room control with communication and occupancy detection | Individual room control with communication and occupancy detection | Régulation individuelle par pièce avec communication et détection d’occupation | Einzelraumregelung mit Kommunikation und Anwesenheitserkennung
overview of services | 675 | 0
overview of services | 676 | 0
overview of services | 677 | Variable speed pump control (external demand signal) | Variable speed pump control (external demand signal) | Commande des pompes à vitesse variable (signal de demande externe) | Pumpensteuerung mit variabler Drehzahl (externes Bedarfssignal)
overview of services | 678 | 0
overview of services | 679 | 0
overview of services | 680 | 0
overview of services | 681 | Sequencing based on dynamic priority list, including external signals from grid | Sequencing based on dynamic priority list, including external signals from grid | Régulation selon priorités calculées dynamiquement ET selon les ordres reçus du réseau | Sequenzierung auf der Grundlage einer dynamischen Prioritätenliste, einschließlich externer Signale vom Netz
overview of services | 682 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Remontée centralisée ou déportée d'indicateurs incluant prévisions, comparaisons, identification de dérives et gestion prévisionnelle | Zentrale oder ferngesteuerte Berichterstattung über die Leistungsbewertung, einschließlich Prognosen und/oder Benchmarking; einschließlich vorausschauendes Management und Fehlererkennung
overview of services | 683 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | Pilotage optimisé du système de refroidissement selon des prévisions locales et des ordres de la part du réseau | Optimierte Steuerung des Kühlsystems auf der Grundlage lokaler Vorhersagen und Netzsignale (z. B. durch modellprädiktive Steuerung)
overview of services | 684 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | Régulation par zones en fonction de données venant de capteurs de qualité de l'air (CO2, COV...) avec débit d’air régulé par registres | Lokale Bedarfssteuerung auf der Grundlage von Luftqualitätssensoren (CO2, VOC,...) mit lokalem Durchfluss von/zu der Zone, der durch Klappen geregelt wird
overview of services | 685 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | Régulation automatique du débit ou de la pression avec réinitialisation de la pression : charge en fonction des alimentations du débit d'air selon les besoins pour toutes les pièces communicantes (pour les systèmes à volume d'air variable avec VFD) | Automatische Volumenstrom- oder Druckregelung mit Druckrückstellung: Lastabhängige Versorgung des Luftstroms für den Bedarf aller angeschlossenen Räume (bei variablen Luftmengensystemen mit VFD).
overview of services | 686 | 0
overview of services | 687 | 0
overview of services | 688 | 0
overview of services | 689 | 0
overview of services | 690 | 0
overview of services | 691 | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | Modulation automatique intégrant du pilotage par scénario (par intervalle de temps, en fonction de la luminosité, de la température de la lumière, et possibilité d'adapter l’éclairage en fonction de l’utilisation des locaux, des besoins et applications) | Automatisches Dimmen mit szenenbasierter Lichtsteuerung (in Zeitintervallen werden dynamische und angepasste Lichtszenen eingestellt, z. B. in Bezug auf die Beleuchtungsstärke, , unterschiedliche korrelierte Farbtemperaturen (CCT), und die Möglichkeit, die Lichtverteilung im Raum zu verändern, z . B. je nach Design, menschlichen Bedürfnissen oder Sehaufgaben)
overview of services | 692 | Predictive blind control (e.g. based on weather forecast) | Predictive blind control (e.g. based on weather forecast) | Contrôle prédictif des protections solaires (ex: en fonction de la météo) | Prädiktive Jalousiesteuerung (z. B. auf der Grundlage der Wettervorhersage)
overview of services | 693 | 0
overview of services | 694 | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | Position de chaque produit, détection des défauts, maintenance prédictive, données temps-réel et historisées (vent, luminosité, température) | Position der einzelnen Produkte, Fehlererkennung, vorausschauende Wartung, Echtzeit- und historische Sensordaten (Wind, Lux, Temperatur...)
overview of services | 695 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Evaluation de performance incluant prévisions et/ou comparaisons, identification de dérives et gestion prévisionnelle | Leistungsbewertung, einschließlich Vorhersage und/oder Benchmarking; einschließlich vorausschauendes Management und Fehlererkennung
overview of services | 696 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | Stockage d'énergie sur site (par exemple, batterie ou stockage thermique) avec optimisation de l'utilisation de l'électricité produite localement et possibilité d'injection dans le réseau | Vor-Ort-Energiespeicherung (z. B. elektrische Batterie oder thermische Speicherung) mit Steuerung zur Optimierung der Nutzung des lokal erzeugten Stroms und Möglichkeit der Rückspeisung ins Netz
overview of services | 697 | 0
overview of services | 698 | 0
overview of services | 699 | 0
overview of services | 700 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | Evaluation de performance incluant prévisions et/ou comparaisons, identification de dérives et gestion prévisionnelle | Leistungsbewertung, einschließlich Vorhersage und/oder Benchmarking; einschließlich vorausschauendes Management und Fehlererkennung
overview of services | 701 | real-time feedback or benchmarking on appliance level with automated personalized recommendations | real-time feedback or benchmarking on appliance level with automated personalized recommendations | Retour d'information en temps réel ou analyse comparative au niveau des appareils avec recommandations personnalisées automatisées | Echtzeit-Feedback oder Benchmarking auf Geräteebene mit automatischen personalisierten Empfehlungen
overview of services | 702 | >50% of parking spaces has recharging point | >50% of parking spaces has recharging point | Plus de 50% des places de parking ont une borne de recharge | >50% der Parkplätze haben eine Aufladestation
overview of services | 703 | 0
overview of services | 704 | 0
overview of services | 705 | 0
overview of services | 706 | 0
overview of services | 707 | 0
overview of services | 708 | 0
overview of services | 709 | 0
overview of services | 710 | 0
overview of services | 711 | Scheduled override of DSM control and reactivation with optimised control | Scheduled override of DSM control and reactivation with optimised control | Préemption et réactivation programmée du contrôle de gestion de la demande avec régulation optimisée | Zeitgesteuertes Außerkraftsetzen der DSM-Steuerung und Wiedereinschalten mit optimierter Steuerung
overview of services | 712 | 0
overview of services | 713 | part of the method A: 1 - YES; 0 - NO | part of the method A: 1 - YES; 0 - NO | Fait partie de la méthode A: 1-OUI; 0-NON | Teil der Methode A: 1 - JA; 0 - NEIN
overview of services | 714 | part of the method B: 1 - YES; 0 - NO | part of the method B: 1 - YES; 0 - NO | Fait partie de la méthode B: 1-OUI; 0-NON | Teil der Methode B: 1 - JA; 0 - NEIN
overview of services | 715 | part of the custom services list?: 1 - YES; 0 - NO | part of the custom services list?: 1 - YES; 0 - NO | Fait partie des services sur-mesure: 1-OUI; 0-NON | Teil der Liste der benutzerdefinierten Dienste?: 1 - JA; 0 - NEIN
overview of services | 716 | Preconditions / Dependency on other services or building types | Preconditions / Dependency on other services or building types | Conditionnalité / Dépendance d'autres services ou type de bâtiment | Voraussetzungen/Abhängigkeit von anderen Dienstleistungen oder Gebäudetypen
overview of services | 717 | 0
overview of services | 718 | 0
overview of services | 719 | Triage: not relevant in case of TABS. | Triage: not relevant in case of TABS. | Triage: non pertinent pour des systèmes thermoactifs (TABS) | Triage: im Falle von TABS nicht relevant.
overview of services | 720 | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | Triage: pertinent seulement pour des systèmes thermoactifs (TABS). Principalement limité aux bâtiments non résidentiels | Triage: nur im Falle von TABS relevant. Meistens auf Nichtwohngebäude beschränkt
overview of services | 721 | Not applicable in case of individual heaters (e.g. stoves) | Not applicable in case of individual heaters (e.g. stoves) | Applicable uniquement en cas de chauffages individuels | Entfällt bei Einzelheizgeräten (z. B. Öfen)
overview of services | 722 | Only applicable for hydronic heating systems | Only applicable for hydronic heating systems | Applicable uniquement en cas de système de chauffage hydronique | Gilt nur für Warmwasserheizsysteme
overview of services | 723 | Only applicable in case thermal energy storage is present. | Only applicable in case thermal energy storage is present. | Applicable uniquement en cas de présence de stockage d'énergie thermique | Gilt nur, wenn ein thermischer Energiespeicher vorhanden ist.
overview of services | 724 | Only applicable in case of combustion heater or district heating | Only applicable in case of combustion heater or district heating | Applicable uniquement pour chauffage avec combustion ou réseau de chaleur | Gilt nur für Verbrennungsheizungen oder Fernwärme
overview of services | 725 | Only applicable in case of heat pumps | Only applicable in case of heat pumps | Applicable uniquement pour pompe à chaleur | Gilt nur für Wärmepumpen
overview of services | 726 | Only applicable in case of multiple heat generators, mostly restricted to large buildings | Only applicable in case of multiple heat generators, mostly restricted to large buildings | Applicable uniquement en cas de générateurs de chaleur multiples (principalement pour des grands bâtiments) | Nur anwendbar im Falle mehrerer Wärmeerzeuger, meist auf große Gebäude beschränkt
overview of services | 727 | 0
overview of services | 728 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated | La nature de l'algorithme de contrôle doit pouvoir être inspectée. | Die Überprüfbarkeit der Art des Kontrollalgorithmus müsste erleichtert werden
overview of services | 729 | Only applicable in case of DHW storage with electric heating | Only applicable in case of DHW storage with electric heating | Applicable uniquement en cas de stockage d'ECS avec chauffage électrique | Gilt nur für Trinkwarmwasserspeicher mit Elektroheizung
overview of services | 730 | Only applicable in case of DHW storage with non-electrical heat generation | Only applicable in case of DHW storage with non-electrical heat generation | Applicable uniquement en cas de stockage d'ECS avec chauffage non-électrique | Gilt nur bei Trinkwarmwasserspeicherung mit nicht-elektrischer Wärmeerzeugung
overview of services | 731 | Only applicable in case of DHW storage with solar collector | Only applicable in case of DHW storage with solar collector | Applicable uniquement en cas de stockage d'ECS avec collecteur solaire | Gilt nur für Trinkwarmwasserspeicher mit Solarkollektor
overview of services | 732 | Only applicable in case of multiple heat generators, mostly restricted to large buildings | Only applicable in case of multiple heat generators, mostly restricted to large buildings | Applicable uniquement en cas de générateurs de chaleur multiples (principalement pour des grands bâtiments) | Nur anwendbar im Falle mehrerer Wärmeerzeuger, meist auf große Gebäude beschränkt
overview of services | 733 | 0
overview of services | 734 | Only applicable in case mechanical cooling systems are present | Only applicable in case mechanical cooling systems are present | Applicable uniquement si des systèmes mécaniques de refroidissement sont présents | Nur anwendbar, wenn mechanische Kühlsysteme vorhanden sind
overview of services | 735 | Only applicable in case mechanical cooling systems based on TABS are present | Only applicable in case mechanical cooling systems based on TABS are present | Applicable uniquement en cas de présence de systèmes de refroidissement mécaniques basés sur des systèmes thermoactifs (TABS) | Nur anwendbar, wenn mechanische Kühlsysteme auf der Grundlage von TABS vorhanden sind
overview of services | 736 | Only applicable in case mechanical cooling systems with hydronic distribution system are present | Only applicable in case mechanical cooling systems with hydronic distribution system are present | Applicable uniquement en cas de présence de systèmes de refroidissement mécaniques avec un système de distribution hydronique | Nur anwendbar, wenn mechanische Kühlsysteme mit hydronischem Verteilungssystem vorhanden sind
overview of services | 737 | Only applicable in case mechanical cooling systems with hydronic distribution system are present | Only applicable in case mechanical cooling systems with hydronic distribution system are present | Applicable uniquement en cas de présence de systèmes de refroidissement mécaniques avec un système de distribution hydronique | Nur anwendbar, wenn mechanische Kühlsysteme mit hydronischem Verteilungssystem vorhanden sind
overview of services | 738 | Only applicable in case mechanical cooling systems are present | Only applicable in case mechanical cooling systems are present | Applicable uniquement si des systèmes mécaniques de refroidissement sont présents | Nur anwendbar, wenn mechanische Kühlsysteme vorhanden sind
overview of services | 739 | Only applicable in case mechanical cooling systems are present ánd include TES systems | Only applicable in case mechanical cooling systems are present ánd include TES systems | Applicable uniquement si des systèmes mécaniques de refroidissement sont présents et contiennent un système de stockage thermique | Gilt nur, wenn mechanische Kühlsysteme vorhanden sind und TES-Systeme umfassen.
overview of services | 740 | Only applicable in case mechanical cooling systems are present | Only applicable in case mechanical cooling systems are present | Applicable uniquement si des systèmes mécaniques de refroidissement sont présents | Nur anwendbar, wenn mechanische Kühlsysteme vorhanden sind
overview of services | 741 | Only applicable in case multiple mechanical cooling systems are present | Only applicable in case multiple mechanical cooling systems are present | Applicable uniquement si plusieurs systèmes mécaniques de refroidissement sont présents | Nur anwendbar, wenn mehrere mechanische Kühlsysteme vorhanden sind
overview of services | 742 | Only applicable in case mechanical cooling systems are present | Only applicable in case mechanical cooling systems are present | Applicable uniquement si des systèmes mécaniques de refroidissement sont présents | Nur anwendbar, wenn mechanische Kühlsysteme vorhanden sind
overview of services | 743 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated | La nature de l'algorithme de contrôle doit pouvoir être inspectée. | Die Überprüfbarkeit der Art des Kontrollalgorithmus müsste erleichtert werden
overview of services | 744 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 745 | Only in case of mechanical ventilation | Only in case of mechanical ventilation | Applicable uniquement en cas de ventilation mécanique | Nur im Falle einer mechanischer Lüftung
overview of services | 746 | Only in case of mechanical ventilation with heat recovery | Only in case of mechanical ventilation with heat recovery | Applicable uniquement en cas de ventilation avec récupération de chaleur | Nur bei mechanischer Lüftung mit Wärmerückgewinnung
overview of services | 747 | Only in case of mechanical ventilation which supplies heating | Only in case of mechanical ventilation which supplies heating | Applicable uniquement en cas de ventilation mécanique qui alimente le chauffage | Nur bei mechanischer Lüftung, die die Heizung versorgt
overview of services | 748 | Only in case of mechanical or hybrid ventilation | Only in case of mechanical or hybrid ventilation | Applicable uniquement en cas de ventilation mécanique ou hybride | Nur bei mechanischer oder hybrider Beatmung
overview of services | 749 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 750 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 751 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 752 | Only applicable in case movable shades, screens or blinds are present | Only applicable in case movable shades, screens or blinds are present | Applicable uniquement en cas de protections solaires mobiles | Gilt nur, wenn bewegliche Jalousien, Rollos oder Rollläden vorhanden sind.
overview of services | 753 | 0
overview of services | 754 | Only applicable in case movable shades, screens or blinds are present | Only applicable in case movable shades, screens or blinds are present | Applicable uniquement en cas de protections solaires mobiles | Gilt nur, wenn bewegliche Jalousien, Rollos oder Rollläden vorhanden sind.
overview of services | 755 | Only applicable in case of local energy generation | Only applicable in case of local energy generation | Applicable uniquement en cas de production locale d'énergie | Gilt nur für die lokale Energieerzeugung
overview of services | 756 | Only applicable in case of local energy generation | Only applicable in case of local energy generation | Applicable uniquement en cas de production locale d'énergie | Gilt nur für die lokale Energieerzeugung
overview of services | 757 | Only applicable in case of local energy generation | Only applicable in case of local energy generation | Applicable uniquement en cas de production locale d'énergie | Gilt nur für die lokale Energieerzeugung
overview of services | 758 | Only applicable in case of CHP | Only applicable in case of CHP | Applicable uniquement en cas de cogénération | Gilt nur im Falle von KWK
overview of services | 759 | Only applicable in case of local energy storage | Only applicable in case of local energy storage | Applicable uniquement en cas de stockage local d'énergie | Nur anwendbar bei lokaler Energiespeicherung
overview of services | 760 | Only applicable in case of local energy storage | Only applicable in case of local energy storage | Applicable uniquement en cas de stockage local d'énergie | Nur anwendbar bei lokaler Energiespeicherung
overview of services | 761 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 762 | Only to be assessed if parking spots available on site | Only to be assessed if parking spots available on site | A évaluer uniquement si des places de parking sont disponibles sur le site | Nur zu bewerten, wenn vor Ort Parkplätze vorhanden sind
overview of services | 763 | Only to be assessed if EV charging available on site | Only to be assessed if EV charging available on site | A évaluer uniquement si des places de parking sont disponibles sur le site | Nur zu bewerten, wenn EV-Ladestationen am Standort verfügbar sind
overview of services | 764 | Only to be assessed if EV charging available on site | Only to be assessed if EV charging available on site | A évaluer uniquement si des places de parking sont disponibles sur le site | Nur zu bewerten, wenn EV-Ladestationen am Standort verfügbar sind
overview of services | 765 | 0
overview of services | 766 | 0
overview of services | 767 | 0
overview of services | 768 | 0
overview of services | 769 | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Pour le niveau 2, la nature de l'algorithme de contrôle doit pouvoir être inspectée. Service 7.5 de EN15232-1-17. Impacts moyens calculés à partir de différentes simulations de facteurs du système de GTB dans EN15232. | Die Inspektion der Art des Regelalgorithmus müsste für Stufe 2 erleichtert werden. Dienstleistung 7.5 in EN15232-1-17. Durchschnittliche Auswirkungen, die aus mehreren Simulationen abgeleitet werden, um BACS-Faktoren in EN15232 zu erzeugen.
overview of services | 770 | 0
overview of services | 771 | 0
overview of services | 772 | Always to be assessed | Always to be assessed | A évaluer systématiquement | Immer zu bewerten
overview of services | 773 | 0
overview of services | 774 | 0
overview of services | 775 | 0
overview of services | 776 | H | H | H | H
overview of services | 777 | H | H | H | H
overview of services | 778 | H | H | H | H
overview of services | 779 | H | H | H | H
overview of services | 780 | H | H | H | H
overview of services | 781 | H | H | H | H
overview of services | 782 | H | H | H | H
overview of services | 783 | H | H | H | H
overview of services | 784 | H | H | H | H
overview of services | 785 | H | H | H | H
overview of services | 786 | DHW | DHW | DHW | DHW
overview of services | 787 | DHW | DHW | DHW | DHW
overview of services | 788 | DHW | DHW | DHW | DHW
overview of services | 789 | DHW | DHW | DHW | DHW
overview of services | 790 | DHW | DHW | DHW | DHW
overview of services | 791 | C | C | C | C
overview of services | 792 | C | C | C | C
overview of services | 793 | C | C | C | C
overview of services | 794 | C | C | C | C
overview of services | 795 | C | C | C | C
overview of services | 796 | C | C | C | C
overview of services | 797 | C | C | C | C
overview of services | 798 | C | C | C | C
overview of services | 799 | C | C | C | C
overview of services | 800 | C | C | C | C
overview of services | 801 | V | V | V | V
overview of services | 802 | V | V | V | V
overview of services | 803 | V | V | V | V
overview of services | 804 | V | V | V | V
overview of services | 805 | V | V | V | V
overview of services | 806 | V | V | V | V
overview of services | 807 | L | L | L | L
overview of services | 808 | L | L | L | L
overview of services | 809 | DE | DE | DE | DE
overview of services | 810 | DE | DE | DE | DE
overview of services | 811 | DE | DE | DE | DE
overview of services | 812 | E | E | E | E
overview of services | 813 | E | E | E | E
overview of services | 814 | E | E | E | E
overview of services | 815 | E | E | E | E
overview of services | 816 | E | E | E | E
overview of services | 817 | E | E | E | E
overview of services | 818 | E | E | E | E
overview of services | 819 | EV | EV | EV | EV
overview of services | 820 | EV | EV | EV | EV
overview of services | 821 | EV | EV | EV | EV
overview of services | 822 | MC | MC | MC | MC
overview of services | 823 | MC | MC | MC | MC
overview of services | 824 | MC | MC | MC | MC
overview of services | 825 | MC | MC | MC | MC
overview of services | 826 | MC | MC | MC | MC
overview of services | 827 | MC | MC | MC | MC
overview of services | 828 | MC | MC | MC | MC
overview of services | 829 | MC | MC | MC | MC
| 830 | North Europe | North Europe | Europe du Nord | Nordeuropa
| 831 | West Europe | West Europe | Europe de l'Ouest | Westeuropa
| 832 | South Europe | South Europe | Europe du Sud | Südeuropa
| 833 | North-East Europe | North-East Europe | Europe du Nord-Est | Nord-Ost-Europa
| 834 | South-East Europe | South-East Europe | Europe du Sud-Est | Südosteuropa
| 835 | Error message | Error message | Message d'erreur | Fehlermeldung
| 836 | please enter a valid functionality level | please enter a valid functionality level | Veuillez entrer un niveau de fonctionnalité valide | Bitte geben Sie eine gültige Funktionsstufe ein
| 837 | error, please check functionality levels | error, please check functionality levels | Erreur, veuillez vérifier les niveaux de fonctionnalité | Fehler, bitte überprüfen Sie die Funktionsebenen
service list - 5 extra service per domain | 838 | Heating | Heating | Chauffage | Heizung
service list - 5 extra service per domain | 839 | Heating | Heating | Chauffage | Heizung
service list - 5 extra service per domain | 840 | Heating | Heating | Chauffage | Heizung
service list - 5 extra service per domain | 841 | Heating | Heating | Chauffage | Heizung
service list - 5 extra service per domain | 842 | Heating | Heating | Chauffage | Heizung
service list - 5 extra service per domain | 843 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
service list - 5 extra service per domain | 844 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
service list - 5 extra service per domain | 845 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
service list - 5 extra service per domain | 846 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
service list - 5 extra service per domain | 847 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
service list - 5 extra service per domain | 848 | Cooling | Cooling | Refroidissement | Kühlung
service list - 5 extra service per domain | 849 | Cooling | Cooling | Refroidissement | Kühlung
service list - 5 extra service per domain | 850 | Cooling | Cooling | Refroidissement | Kühlung
service list - 5 extra service per domain | 851 | Cooling | Cooling | Refroidissement | Kühlung
service list - 5 extra service per domain | 852 | Cooling | Cooling | Refroidissement | Kühlung
service list - 5 extra service per domain | 853 | Ventilation | Ventilation | Ventilation | Belüftung
service list - 5 extra service per domain | 854 | Ventilation | Ventilation | Ventilation | Belüftung
service list - 5 extra service per domain | 855 | Ventilation | Ventilation | Ventilation | Belüftung
service list - 5 extra service per domain | 856 | Ventilation | Ventilation | Ventilation | Belüftung
service list - 5 extra service per domain | 857 | Ventilation | Ventilation | Ventilation | Belüftung
service list - 5 extra service per domain | 858 | Lighting | Lighting | Eclairage | Beleuchtung
service list - 5 extra service per domain | 859 | Lighting | Lighting | Eclairage | Beleuchtung
service list - 5 extra service per domain | 860 | Lighting | Lighting | Eclairage | Beleuchtung
service list - 5 extra service per domain | 861 | Lighting | Lighting | Eclairage | Beleuchtung
service list - 5 extra service per domain | 862 | Lighting | Lighting | Eclairage | Beleuchtung
service list - 5 extra service per domain | 863 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
service list - 5 extra service per domain | 864 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
service list - 5 extra service per domain | 865 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
service list - 5 extra service per domain | 866 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
service list - 5 extra service per domain | 867 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
service list - 5 extra service per domain | 868 | Electricity | Electricity | Electricité | Elektrizität
service list - 5 extra service per domain | 869 | Electricity | Electricity | Electricité | Elektrizität
service list - 5 extra service per domain | 870 | Electricity | Electricity | Electricité | Elektrizität
service list - 5 extra service per domain | 871 | Electricity | Electricity | Electricité | Elektrizität
service list - 5 extra service per domain | 872 | Electricity | Electricity | Electricité | Elektrizität
service list - 5 extra service per domain | 873 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
service list - 5 extra service per domain | 874 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
service list - 5 extra service per domain | 875 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
service list - 5 extra service per domain | 876 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
service list - 5 extra service per domain | 877 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
service list - 5 extra service per domain | 878 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
service list - 5 extra service per domain | 879 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
service list - 5 extra service per domain | 880 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
service list - 5 extra service per domain | 881 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
service list - 5 extra service per domain | 882 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
service list - simplied service modification | 883 | Control heat production facilities | Control heat production facilities | Commande des installations de production de chaleur | Kontrolle von Wärmeerzeugungsanlagen
service list - simplied service modification | 884 | Storage and shifting of thermal energy | Storage and shifting of thermal energy | Stockage et déplacement de l'énergie thermique | Speicherung und Verlagerung von Wärmeenergie
service list - simplied service modification | 885 | None | None | Aucun | Keine
service list - simplied service modification | 886 | HW storage vessels available | HW storage vessels available | Ballons d'eau chaude disponibles | HW-Lagerbehälter verfügbar
service list - simplied service modification | 887 | HW storage vessels controlled based on external signals (from BACS or grid) | HW storage vessels controlled based on external signals (from BACS or grid) | Ballons d'eau chaude commandés par des signaux externes (venant du système d’automatisation et de contrôle du bâtiment ou du réseau) | HW-Lagerbehälter, die auf der Grundlage externer Signale (von BACS oder dem Netz) gesteuert werden
service list - simplied service modification | 888 | 0
service list - simplied service modification | 889 | 0
service list - simplied service modification | 890 | Flexibility DHW production facilities | Flexibility DHW production facilities | Flexibilité des installations de production d'eau chaude sanitaire | Flexibilität Trinkwarmwasserbereitungsanlagen
service list - simplied service modification | 891 | Control of DHW storage charging | Control of DHW storage charging | Commande de la charge du stockage de l'eau chaude sanitaire | Steuerung der Trinkwarmwasserspeicherladung
service list - simplied service modification | 892 | None | None | Aucun | Keine
service list - simplied service modification | 893 | HW storage vessels available | HW storage vessels available | Ballons d'eau chaude sanitaire disponibles | HW-Lagerbehälter verfügbar
service list - simplied service modification | 894 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | Commande automatique de la charge en fonction de la disponibilité locale des énergies renouvelables ou des informations provenant du réseau électrique (flexibilité de la demande, effacements) | Automatische Ladesteuerung basierend auf der lokalen Verfügbarkeit von erneuerbaren Energien oder Informationen aus dem Stromnetz (DR, DSM)
service list - extra service code | 895 | H-E1 | H-E1 | H-E1 | H-E1
service list - extra service code | 896 | H-E2 | H-E2 | H-E2 | H-E2
service list - extra service code | 897 | H-E3 | H-E3 | H-E3 | H-E3
service list - extra service code | 898 | H-E4 | H-E4 | H-E4 | H-E4
service list - extra service code | 899 | H-E5 | H-E5 | H-E5 | H-E5
service list - extra service code | 900 | DHW-E1 | DHW-E1 | DHW-E1 | DHW-E1
service list - extra service code | 901 | DHW-E2 | DHW-E2 | DHW-E2 | DHW-E2
service list - extra service code | 902 | DHW-E3 | DHW-E3 | DHW-E3 | DHW-E3
service list - extra service code | 903 | DHW-E4 | DHW-E4 | DHW-E4 | DHW-E4
service list - extra service code | 904 | DHW-E5 | DHW-E5 | DHW-E5 | DHW-E5
service list - extra service code | 905 | C-E1 | C-E1 | C-E1 | C-E1
service list - extra service code | 906 | C-E2 | C-E2 | C-E2 | C-E2
service list - extra service code | 907 | C-E3 | C-E3 | C-E3 | C-E3
service list - extra service code | 908 | C-E4 | C-E4 | C-E4 | C-E4
service list - extra service code | 909 | C-E5 | C-E5 | C-E5 | C-E5
service list - extra service code | 910 | V-E1 | V-E1 | V-E1 | V-E1
service list - extra service code | 911 | V-E2 | V-E2 | V-E2 | V-E2
service list - extra service code | 912 | V-E3 | V-E3 | V-E3 | V-E3
service list - extra service code | 913 | V-E4 | V-E4 | V-E4 | V-E4
service list - extra service code | 914 | V-E5 | V-E5 | V-E5 | V-E5
service list - extra service code | 915 | L-E1 | L-E1 | L-E1 | L-E1
service list - extra service code | 916 | L-E2 | L-E2 | L-E2 | L-E2
service list - extra service code | 917 | L-E3 | L-E3 | L-E3 | L-E3
service list - extra service code | 918 | L-E4 | L-E4 | L-E4 | L-E4
service list - extra service code | 919 | L-E5 | L-E5 | L-E5 | L-E5
service list - extra service code | 920 | DE-E1 | DE-E1 | DE-E1 | DE-E1
service list - extra service code | 921 | DE-E2 | DE-E2 | DE-E2 | DE-E2
service list - extra service code | 922 | DE-E3 | DE-E3 | DE-E3 | DE-E3
service list - extra service code | 923 | DE-E4 | DE-E4 | DE-E4 | DE-E4
service list - extra service code | 924 | DE-E5 | DE-E5 | DE-E5 | DE-E5
service list - extra service code | 925 | E-E1 | E-E1 | E-E1 | E-E1
service list - extra service code | 926 | E-E2 | E-E2 | E-E2 | E-E2
service list - extra service code | 927 | E-E3 | E-E3 | E-E3 | E-E3
service list - extra service code | 928 | E-E4 | E-E4 | E-E4 | E-E4
service list - extra service code | 929 | E-E5 | E-E5 | E-E5 | E-E5
service list - extra service code | 930 | EV-E1 | EV-E1 | EV-E1 | EV-E1
service list - extra service code | 931 | EV-E2 | EV-E2 | EV-E2 | EV-E2
service list - extra service code | 932 | EV-E3 | EV-E3 | EV-E3 | EV-E3
service list - extra service code | 933 | EV-E4 | EV-E4 | EV-E4 | EV-E4
service list - extra service code | 934 | EV-E5 | EV-E5 | EV-E5 | EV-E5
service list - extra service code | 935 | MC-E1 | MC-E1 | MC-E1 | MC-E1
service list - extra service code | 936 | MC-E2 | MC-E2 | MC-E2 | MC-E2
service list - extra service code | 937 | MC-E3 | MC-E3 | MC-E3 | MC-E3
service list - extra service code | 938 | MC-E4 | MC-E4 | MC-E4 | MC-E4
service list - extra service code | 939 | MC-E5 | MC-E5 | MC-E5 | MC-E5
calculation | 940 | Enable/disable this service manually for your assessment: 0-disable; 1-enable; blank-use default status of this service in your selected method | Enable/disable this service manually for your assessment: 0-disable; 1-enable; blank-use default status of this service in your selected method | Activer/désactiver ce service manuellement pour votre évaluation: 0- désactiver; 1- activer; vide- statut par défaut de ce service selon la méthode sélectionnée | Aktivieren/deaktivieren Sie diesen Dienst manuell für Ihre Bewertung: 0-deaktivieren; 1-aktivieren; leer-den Standardstatus dieses Dienstes in der von Ihnen gewählten Methode verwenden
calculation | 941 | Service to be included in the calculation sheet | Service to be included in the calculation sheet | Service à inclure dans la feuille de calcul | In den Berechnungsbogen aufzunehmende Leistung
calculation | 942 | Service included in the selected method (A/B/custom): 0 - not included, 1 - included | Service included in the selected method (A/B/custom): 0 - not included, 1 - included | Service inclus dans la méthode sélectionnée (A, B ou sur-mesure): 0- non inclus; 1- inclus | In der gewählten Methode enthaltener Dienst (A/B/custom): 0 - nicht enthalten, 1 - enthalten
calculation | 943 | Service applicable in your building? - to be assessed by the assessor: 1 - applicable; 0 - not applicable | Service applicable in your building? - to be assessed by the assessor: 1 - applicable; 0 - not applicable | Service applicable dans le bâtiment? - A estimer par l'évaluateur: 1- applicable; 0 - non applicable | Ist die Dienstleistung in Ihrem Gebäude anwendbar? - vom Prüfer zu bewerten: 1 - anwendbar; 0 - nicht anwendbar
calculation | 944 | Main functionality level as inspected by SRI assessor | Main functionality level as inspected by SRI assessor | Niveau de fonctionnalité principal estimé par l'évaluateur | Hauptfunktionalitätsebene gemäß Inspektion durch den SRI-Prüfer
calculation | 945 | share (default = 100% means applicable throughout the building) | share (default = 100% means applicable throughout the building) | Part (par défaut = 100%, c'est-à-dire applicable à l'ensemble du bâtiment) | Anteil (Standardwert = 100 % bedeutet, dass er für das gesamte Gebäude gilt)
calculation | 946 | Optional: additional functionality level in part of the building | Optional: additional functionality level in part of the building | Facultatif: niveau additionnel de fonctionnalité dans une partie du bâtiment | Optional: zusätzliche Funktionsebene in einem Teil des Gebäudes
calculation | 947 | Share of additional functionality level | Share of additional functionality level | Part du niveau additionnel de fonctionnalité | Anteil der zusätzlichen Funktionsebene
calculation | 948 | Warnings | Warnings | Avertissements | Warnungen
calculation | 949 | building type --> | building type --> | Type de bâtiment --> | Gebäudetyp -->
calculation | 950 | Service part of the method and domain selection? | Service part of the method and domain selection? | Service qui fait partie de la méthode et des domaines sélectionnés | Dienstleistung Teil der Methoden- und Bereichsauswahl?
calculation | 951 | Optional feedback: Estimated assessment time (minutes) | Optional feedback: Estimated assessment time (minutes) | Facultatif: durée estimée de l'évaluation (minutes) | Optionales Feedback: Geschätzte Bewertungszeit (Minuten)
calculation | 952 | Optional: assessor's comments | Optional: assessor's comments | Facultatif: commentaires de l'évaluateur | Fakultativ: Kommentare des Prüfers
calculation | 953 | Service applicable? | Service applicable? | Service applicable? | Dienstleistung anwendbar?
Weightings tab | 954 | USER DEFINED | USER DEFINED | Défini par l'utilisateur | BENUTZERDEFINIERT
Weightings tab | 955 | DOMAIN WEIGHTINGS | DOMAIN WEIGHTINGS | Pondération des domaines | BEREICHSGEWICHTUNGEN
Weightings tab | 956 | Heating | Heating | Chauffage | Heizung
Weightings tab | 957 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
Weightings tab | 958 | Cooling | Cooling | Refroidissement | Kühlung
Weightings tab | 959 | Ventilation | Ventilation | Ventilation | Belüftung
Weightings tab | 960 | Lighting | Lighting | Eclairage | Beleuchtung
Weightings tab | 961 | Electricity | Electricity | Electricité | Elektrizität
Weightings tab | 962 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
Weightings tab | 963 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
Weightings tab | 964 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
Weightings tab | 965 | 0
Weightings tab | 966 | Energy efficiency | Energy efficiency | Efficacité énergétique | Energie-Effizienz
Weightings tab | 967 | Energy flexibility and storage | Energy flexibility and storage | Flexibilité énergétique et stockage de l’énergie | Energieflexibilität und -speicherung
Weightings tab | 968 | Comfort | Comfort | Confort | Komfort
Weightings tab | 969 | Convenience | Convenience | Caractère pratique | Bequemlichkeit
Weightings tab | 970 | Health, well-being and accessibility | Health, well-being and accessibility | Santé, bien-être et accessibilité | Gesundheit, Wohlbefinden und Zugänglichkeit
Weightings tab | 971 | Maintenance and fault prediction | Maintenance and fault prediction | Entretien et prédiction des pannes | Wartung und Fehlervorhersage
Weightings tab | 972 | Information to occupants | Information to occupants | Information des occupants | Informationen für die Gebäudenutzer
Weightings tab | 973 | 0
Weightings tab | 974 | please check values, each domain weighting should add up to 100% | please check values, each domain weighting should add up to 100% | Veuillez vérifier les valeurs, la somme des pondérations de chaque domaine doit atteindre 100%. | Bitte überprüfen Sie die Werte, die Gewichtung der einzelnen Bereiche sollte 100% ergeben.
Weightings tab | 975 | IMPACT WEIGHTINGS | IMPACT WEIGHTINGS | Pondération des impacts | AUSWIRKUNGSGEWICHTUNGEN
Weightings tab | 976 | NOTE: some cells are set to zero and cannot be changed. This means that for these domains, the services have no impact on the given impact criterion. | NOTE: some cells are set to zero and cannot be changed. This means that for these domains, the services have no impact on the given impact criterion. | NOTE : certaines cellules sont mises à zéro et ne peuvent pas être modifiées. Cela signifie que pour ces domaines, les services n'ont aucun impact sur le critère d'impact donné. | HINWEIS: Einige Zellen sind auf Null gesetzt und können nicht geändert werden. Dies bedeutet, dass die Dienstleistungen für diese Bereiche keine Auswirkungen auf das jeweilige Auswirkungskriterium haben.
Weightings tab | 977 | => no weight should be attributed. | => no weight should be attributed. | => Aucune pondération n'est à attribuer | => es sollte kein Gewicht zugewiesen werden.
calculation | 978 | TRIAGE: 1 - This service affects maximum obtainable score, even if service is not applicable in this building; 0 - This service does not affect maximum obtainable score when not present in building | TRIAGE: 1 - This service affects maximum obtainable score, even if service is not applicable in this building; 0 - This service does not affect maximum obtainable score when not present in building | TRIAGE : 1 - Ce service affecte le score maximum pouvant être obtenu, même si le service n'est pas applicable dans ce bâtiment ; 0 - Ce service n'affecte pas le score maximum pouvant être obtenu s'il n'est pas présent dans le bâtiment. | BEWERTUNG: 1 - Diese Dienstleistung wirkt sich auf die maximal erreichbare Punktzahl aus, auch wenn die Dienstleistung in diesem Gebäude nicht anwendbar ist; 0 - Diese Dienstleistung wirkt sich nicht auf die maximal erreichbare Punktzahl aus, wenn sie im Gebäude nicht vorhanden ist
calculation | 979 | 1 - This domain is present; 2 - This domain is absent but mandatory; 0 - This domain is absent and not mandatory | 1 - This domain is present; 2 - This domain is absent but mandatory; 0 - This domain is absent and not mandatory | 1- Ce domaine est présent; 2- Ce domaine est absent mais obligatoire; 0- Ce domaine est absent et non obligatoire | 1 - Dieser Bereich ist vorhanden; 2 - Dieser Bereich ist nicht vorhanden, aber obligatorisch; 0 - Dieser Bereich ist nicht vorhanden und nicht obligatorisch
Results tab | 980 | Smart Readiness Indicator for Buildings | Smart Readiness Indicator for Buildings | Indicateur du potentiel d’intelligence des bâtiments | Smart Readiness Indicator für Gebäude
Results tab | 981 | The SRI calculations have been performed with an experimental tool. Please note that the scores and the visual presentation of results are solely provided for testing purposes. Using this experimental tool can by no means lead to any claims on an actual score or certificate for a building. | The SRI calculations have been performed with an experimental tool. Please note that the scores and the visual presentation of results are solely provided for testing purposes. Using this experimental tool can by no means lead to any claims on an actual score or certificate for a building. | Les calculs du potentiel d'intelligence ont été effectués avec un outil expérimental. Veuillez noter que les valeurs et la présentation visuelle des résultats sont uniquement fournis à des fins de test. L'utilisation de cet outil expérimental ne permet en aucun cas de prétendre à un score ou à un certificat réel pour un bâtiment. | Die SRI-Berechnungen wurden mit einem experimentellen Werkzeug durchgeführt. Bitte beachten Sie, dass die Werte und die visuelle Darstellung der Ergebnisse ausschließlich zu Testzwecken zur Verfügung gestellt werden. Die Verwendung dieses experimentellen Tools kann in keiner Weise zu einem Anspruch auf eine tatsächliche Bewertung oder ein Zertifikat für ein Gebäude führen.
Results tab | 982 | SRI spreadsheet tool Version 4.5 | SRI spreadsheet tool Version 4.5 | Outil de calcul du potentiel d'intelligence Version 4.5 | SRI-Tabellenkalkulationsprogramm Version 4.5
Results tab | 983 | TOTAL SRI SCORE | TOTAL SRI SCORE | Valeur totale du potentiel d’intelligence | Gesamt-SRI-Punktzahl
Results tab | 984 | IMPACT SCORES | IMPACT SCORES | Valeurs du potentiel d’intelligence par critère d'impact | Auswirkungswerte
| 985 | DOMAIN SCORES | DOMAIN SCORES | Valeurs du potentiel d’intelligence par domaine technique | Bereichspunkte
| 986 | DETAILED SCORES | DETAILED SCORES | Valeurs détaillées | Detaillierte Bewertungen
Individual domain tab | 987 | Domain | Domain | Domaine | Bereich
Individual domain tab | 988 | Heating | Heating | Chauffage | Heizung
Individual domain tab | 989 | Domestic hot water | Domestic hot water | Eau chaude sanitaire | Trinkwarmwasser
Individual domain tab | 990 | Cooling | Cooling | Refroidissement | Kühlung
Individual domain tab | 991 | Ventilation | Ventilation | Ventilation | Belüftung
Individual domain tab | 992 | Lighting | Lighting | Eclairage | Beleuchtung
Individual domain tab | 993 | Dynamic building envelope | Dynamic building envelope | Enveloppe dynamique du bâtiment | Dynamische Gebäudehülle
Individual domain tab | 994 | Electricity | Electricity | Electricité | Elektrizität
Individual domain tab | 995 | Electric vehicle charging | Electric vehicle charging | Recharge des véhicules électriques | Laden von Elektrofahrzeugen
Individual domain tab | 996 | Monitoring and control | Monitoring and control | Suivi et contrôle | Überwachung und Kontrolle
Individual domain tab | 997 | 0
Individual domain tab | 998 | code | code | code | Code
Individual domain tab | 999 | service | service | service | Dienstleistung
Individual domain tab | 1000 | Functionality levels | Functionality levels | Niveaux de fonctionnalité | Funktionsebenen
Individual domain tab | 1001 | level 0 | level 0 | Niveau 0 | Stufe 0
Individual domain tab | 1002 | level 1 | level 1 | Niveau 1 | Stufe 1
Individual domain tab | 1003 | level 2 | level 2 | Niveau 2 | Stufe 2
Individual domain tab | 1004 | level 3 | level 3 | Niveau 3 | Stufe 3
Individual domain tab | 1005 | level 4 | level 4 | Niveau 4 | Stufe 4
Individual domain tab | 1006 | IMPACTS | IMPACTS | IMPACTS | IMPACTS
Individual domain tab | 1007 | Information sources | Information sources | Sources d'information | Informationsquellen
Individual domain tab | 1008 | Standard? | Standard? | Standard? | Standard?
Individual domain tab | 1009 | Service group: | Service group: | Groupe de services | Dienstgruppe:
Individual domain tab | 1010 | SRI CLASS | SRI CLASS | Classe du potentiel d’intelligence | SRI-KLASSE
Individual domain tab | 1011 | AGGREGATED SCORES | AGGREGATED SCORES | Valeurs aggrégées | AGGREGIERTE PUNKTZAHLEN
Individual domain tab | 1012 | Key functionality 1 - building | Key functionality 1 - building | Fonctionnalité principale 1 - bâtiment | Schlüsselfunktionalität 1 - Gebäude
Individual domain tab | 1013 | Key functionality 2 - user | Key functionality 2 - user | Fonctionnalité principale 2 - utilisateur | Schlüsselfunktionalität 2 - Benutzer
Individual domain tab | 1014 | Key functionality 3 - grid | Key functionality 3 - grid | Fonctionnalité principale 3 - réseau | Schlüsselfunktionalität 3 - Gitter
Individual domain tab | 1015 | 0
Individual domain tab | 1016 | 0
Individual domain tab | 1017 | 0
Individual domain tab | 1018 | 0
Individual domain tab | 1019 | 0
| 1020 | User defined service group 1 | User defined service group 1 | Groupe de services définis par l'utilisateur 1 | Benutzerdefinierte Dienstgruppe 1
| 1021 | User defined service group 2 | User defined service group 2 | Groupe de services définis par l'utilisateur 2 | Benutzerdefinierte Dienstgruppe 2
| 1022 | User defined service group 3 | User defined service group 3 | Groupe de services définis par l'utilisateur 3 | Benutzerdefinierte Dienstgruppe 3
| 1023 | User defined service group 4 | User defined service group 4 | Groupe de services définis par l'utilisateur 4 | Benutzerdefinierte Dienstgruppe 4
| 1024 | User defined service group 5 | User defined service group 5 | Groupe de services définis par l'utilisateur 5 | Benutzerdefinierte Dienstgruppe 5
| 1025 | User defined service group 6 | User defined service group 6 | Groupe de services définis par l'utilisateur 6 | Benutzerdefinierte Dienstgruppe 6
| 1026 | User defined service group 7 | User defined service group 7 | Groupe de services définis par l'utilisateur 7 | Benutzerdefinierte Dienstgruppe 7
| 1027 | User defined service group 8 | User defined service group 8 | Groupe de services définis par l'utilisateur 8 | Benutzerdefinierte Dienstgruppe 8
| 1028 | User defined service group 9 | User defined service group 9 | Groupe de services définis par l'utilisateur 9 | Benutzerdefinierte Dienstgruppe 9
| 1029 | User defined service group 10 | User defined service group 10 | Groupe de services définis par l'utilisateur 10 | Benutzerdefinierte Dienstgruppe 10
| 1030 | User defined service group 11 | User defined service group 11 | Groupe de services définis par l'utilisateur 11 | Benutzerdefinierte Dienstgruppe 11
| 1031 | User defined service group 12 | User defined service group 12 | Groupe de services définis par l'utilisateur 12 | Benutzerdefinierte Dienstgruppe 12
| 1032 | User defined service group 13 | User defined service group 13 | Groupe de services définis par l'utilisateur 13 | Benutzerdefinierte Dienstgruppe 13
| 1033 | User defined service group 14 | User defined service group 14 | Groupe de services définis par l'utilisateur 14 | Benutzerdefinierte Dienstgruppe 14
| 1034 | User defined service group 15 | User defined service group 15 | Groupe de services définis par l'utilisateur 15 | Benutzerdefinierte Dienstgruppe 15
| 1035 | User defined service group 16 | User defined service group 16 | Groupe de services définis par l'utilisateur 16 | Benutzerdefinierte Dienstgruppe 16
| 1036 | User defined service group 17 | User defined service group 17 | Groupe de services définis par l'utilisateur 17 | Benutzerdefinierte Dienstgruppe 17
| 1037 | User defined service group 18 | User defined service group 18 | Groupe de services définis par l'utilisateur 18 | Benutzerdefinierte Dienstgruppe 18
| 1038 | User defined service group 19 | User defined service group 19 | Groupe de services définis par l'utilisateur 19 | Benutzerdefinierte Dienstgruppe 19
| 1039 | User defined service group 20 | User defined service group 20 | Groupe de services définis par l'utilisateur 20 | Benutzerdefinierte Dienstgruppe 20
| 1040 | User defined service group 21 | User defined service group 21 | Groupe de services définis par l'utilisateur 21 | Benutzerdefinierte Dienstgruppe 21
| 1041 | User defined service group 22 | User defined service group 22 | Groupe de services définis par l'utilisateur 22 | Benutzerdefinierte Dienstgruppe 22
| 1042 | User defined service group 23 | User defined service group 23 | Groupe de services définis par l'utilisateur 23 | Benutzerdefinierte Dienstgruppe 23
| 1043 | User defined service group 24 | User defined service group 24 | Groupe de services définis par l'utilisateur 24 | Benutzerdefinierte Dienstgruppe 24
| 1044 | User defined service group 25 | User defined service group 25 | Groupe de services définis par l'utilisateur 25 | Benutzerdefinierte Dienstgruppe 25
| 1045 | User defined service group 26 | User defined service group 26 | Groupe de services définis par l'utilisateur 26 | Benutzerdefinierte Dienstgruppe 26
| 1046 | User defined service group 27 | User defined service group 27 | Groupe de services définis par l'utilisateur 27 | Benutzerdefinierte Dienstgruppe 27
| 1047 | User defined service group 28 | User defined service group 28 | Groupe de services définis par l'utilisateur 28 | Benutzerdefinierte Dienstgruppe 28
| 1048 | User defined service group 29 | User defined service group 29 | Groupe de services définis par l'utilisateur 29 | Benutzerdefinierte Dienstgruppe 29
| 1049 | User defined service group 30 | User defined service group 30 | Groupe de services définis par l'utilisateur 30 | Benutzerdefinierte Dienstgruppe 30
| 1050 | User defined service group 31 | User defined service group 31 | Groupe de services définis par l'utilisateur 31 | Benutzerdefinierte Dienstgruppe 31
| 1051 | User defined service group 32 | User defined service group 32 | Groupe de services définis par l'utilisateur 32 | Benutzerdefinierte Dienstgruppe 32
| 1052 | User defined service group 33 | User defined service group 33 | Groupe de services définis par l'utilisateur 33 | Benutzerdefinierte Dienstgruppe 33
| 1053 | User defined service group 34 | User defined service group 34 | Groupe de services définis par l'utilisateur 34 | Benutzerdefinierte Dienstgruppe 34
| 1054 | User defined service group 35 | User defined service group 35 | Groupe de services définis par l'utilisateur 35 | Benutzerdefinierte Dienstgruppe 35
| 1055 | User defined service group 36 | User defined service group 36 | Groupe de services définis par l'utilisateur 36 | Benutzerdefinierte Dienstgruppe 36
| 1056 | User defined service group 37 | User defined service group 37 | Groupe de services définis par l'utilisateur 37 | Benutzerdefinierte Dienstgruppe 37
| 1057 | User defined service group 38 | User defined service group 38 | Groupe de services définis par l'utilisateur 38 | Benutzerdefinierte Dienstgruppe 38
| 1058 | User defined service group 39 | User defined service group 39 | Groupe de services définis par l'utilisateur 39 | Benutzerdefinierte Dienstgruppe 39
| 1059 | User defined service group 40 | User defined service group 40 | Groupe de services définis par l'utilisateur 40 | Benutzerdefinierte Dienstgruppe 40
| 1060 | User defined service group 41 | User defined service group 41 | Groupe de services définis par l'utilisateur 41 | Benutzerdefinierte Dienstgruppe 41
| 1061 | User defined service group 42 | User defined service group 42 | Groupe de services définis par l'utilisateur 42 | Benutzerdefinierte Dienstgruppe 42
| 1062 | User defined service group 43 | User defined service group 43 | Groupe de services définis par l'utilisateur 43 | Benutzerdefinierte Dienstgruppe 43
| 1063 | User defined service group 44 | User defined service group 44 | Groupe de services définis par l'utilisateur 44 | Benutzerdefinierte Dienstgruppe 44
| 1064 | User defined service group 45 | User defined service group 45 | Groupe de services définis par l'utilisateur 45 | Benutzerdefinierte Dienstgruppe 45
| 1065 | User defined smart ready service 1 | User defined smart ready service 1 | Service à potentiel d'intelligence défini par l'utilisateur 1 | Benutzerdefinierter Smart-Ready-Dienst 1
| 1066 | User defined smart ready service 2 | User defined smart ready service 2 | Service à potentiel d'intelligence défini par l'utilisateur 2 | Benutzerdefinierter Smart-Ready-Dienst 2
| 1067 | User defined smart ready service 3 | User defined smart ready service 3 | Service à potentiel d'intelligence défini par l'utilisateur 3 | Benutzerdefinierter Smart-Ready-Dienst 3
| 1068 | User defined smart ready service 4 | User defined smart ready service 4 | Service à potentiel d'intelligence défini par l'utilisateur 4 | Benutzerdefinierter Smart-Ready-Dienst 4
| 1069 | User defined smart ready service 5 | User defined smart ready service 5 | Service à potentiel d'intelligence défini par l'utilisateur 5 | Benutzerdefinierter Smart-Ready-Dienst 5
| 1070 | User defined smart ready service 6 | User defined smart ready service 6 | Service à potentiel d'intelligence défini par l'utilisateur 6 | Benutzerdefinierter Smart-Ready-Dienst 6
| 1071 | User defined smart ready service 7 | User defined smart ready service 7 | Service à potentiel d'intelligence défini par l'utilisateur 7 | Benutzerdefinierter Smart-Ready-Dienst 7
| 1072 | User defined smart ready service 8 | User defined smart ready service 8 | Service à potentiel d'intelligence défini par l'utilisateur 8 | Benutzerdefinierter Smart-Ready-Dienst 8
| 1073 | User defined smart ready service 9 | User defined smart ready service 9 | Service à potentiel d'intelligence défini par l'utilisateur 9 | Benutzerdefinierter Smart-Ready-Dienst 9
| 1074 | User defined smart ready service 10 | User defined smart ready service 10 | Service à potentiel d'intelligence défini par l'utilisateur 10 | Benutzerdefinierter Smart-Ready-Dienst 10
| 1075 | User defined smart ready service 11 | User defined smart ready service 11 | Service à potentiel d'intelligence défini par l'utilisateur 11 | Benutzerdefinierter Smart-Ready-Dienst 11
| 1076 | User defined smart ready service 12 | User defined smart ready service 12 | Service à potentiel d'intelligence défini par l'utilisateur 12 | Benutzerdefinierter Smart-Ready-Dienst 12
| 1077 | User defined smart ready service 13 | User defined smart ready service 13 | Service à potentiel d'intelligence défini par l'utilisateur 13 | Benutzerdefinierter Smart-Ready-Dienst 13
| 1078 | User defined smart ready service 14 | User defined smart ready service 14 | Service à potentiel d'intelligence défini par l'utilisateur 14 | Benutzerdefinierter Smart-Ready-Dienst 14
| 1079 | User defined smart ready service 15 | User defined smart ready service 15 | Service à potentiel d'intelligence défini par l'utilisateur 15 | Benutzerdefinierter Smart-Ready-Dienst 15
| 1080 | User defined smart ready service 16 | User defined smart ready service 16 | Service à potentiel d'intelligence défini par l'utilisateur 16 | Benutzerdefinierter Smart-Ready-Dienst 16
| 1081 | User defined smart ready service 17 | User defined smart ready service 17 | Service à potentiel d'intelligence défini par l'utilisateur 17 | Benutzerdefinierter Smart-Ready-Dienst 17
| 1082 | User defined smart ready service 18 | User defined smart ready service 18 | Service à potentiel d'intelligence défini par l'utilisateur 18 | Benutzerdefinierter Smart-Ready-Dienst 18
| 1083 | User defined smart ready service 19 | User defined smart ready service 19 | Service à potentiel d'intelligence défini par l'utilisateur 19 | Benutzerdefinierter Smart-Ready-Dienst 19
| 1084 | User defined smart ready service 20 | User defined smart ready service 20 | Service à potentiel d'intelligence défini par l'utilisateur 20 | Benutzerdefinierter Smart-Ready-Dienst 20
| 1085 | User defined smart ready service 21 | User defined smart ready service 21 | Service à potentiel d'intelligence défini par l'utilisateur 21 | Benutzerdefinierter Smart-Ready-Dienst 21
| 1086 | User defined smart ready service 22 | User defined smart ready service 22 | Service à potentiel d'intelligence défini par l'utilisateur 22 | Benutzerdefinierter Smart-Ready-Dienst 22
| 1087 | User defined smart ready service 23 | User defined smart ready service 23 | Service à potentiel d'intelligence défini par l'utilisateur 23 | Benutzerdefinierter Smart-Ready-Dienst 23
| 1088 | User defined smart ready service 24 | User defined smart ready service 24 | Service à potentiel d'intelligence défini par l'utilisateur 24 | Benutzerdefinierter Smart-Ready-Dienst 24
| 1089 | User defined smart ready service 25 | User defined smart ready service 25 | Service à potentiel d'intelligence défini par l'utilisateur 25 | Benutzerdefinierter Smart-Ready-Dienst 25
| 1090 | User defined smart ready service 26 | User defined smart ready service 26 | Service à potentiel d'intelligence défini par l'utilisateur 26 | Benutzerdefinierter Smart-Ready-Dienst 26
| 1091 | User defined smart ready service 27 | User defined smart ready service 27 | Service à potentiel d'intelligence défini par l'utilisateur 27 | Benutzerdefinierter Smart-Ready-Dienst 27
| 1092 | User defined smart ready service 28 | User defined smart ready service 28 | Service à potentiel d'intelligence défini par l'utilisateur 28 | Benutzerdefinierter Smart-Ready-Dienst 28
| 1093 | User defined smart ready service 29 | User defined smart ready service 29 | Service à potentiel d'intelligence défini par l'utilisateur 29 | Benutzerdefinierter Smart-Ready-Dienst 29
| 1094 | User defined smart ready service 30 | User defined smart ready service 30 | Service à potentiel d'intelligence défini par l'utilisateur 30 | Benutzerdefinierter Smart-Ready-Dienst 30
| 1095 | User defined smart ready service 31 | User defined smart ready service 31 | Service à potentiel d'intelligence défini par l'utilisateur 31 | Benutzerdefinierter Smart-Ready-Dienst 31
| 1096 | User defined smart ready service 32 | User defined smart ready service 32 | Service à potentiel d'intelligence défini par l'utilisateur 32 | Benutzerdefinierter Smart-Ready-Dienst 32
| 1097 | User defined smart ready service 33 | User defined smart ready service 33 | Service à potentiel d'intelligence défini par l'utilisateur 33 | Benutzerdefinierter Smart-Ready-Dienst 33
| 1098 | User defined smart ready service 34 | User defined smart ready service 34 | Service à potentiel d'intelligence défini par l'utilisateur 34 | Benutzerdefinierter Smart-Ready-Dienst 34
| 1099 | User defined smart ready service 35 | User defined smart ready service 35 | Service à potentiel d'intelligence défini par l'utilisateur 35 | Benutzerdefinierter Smart-Ready-Dienst 35
| 1100 | User defined smart ready service 36 | User defined smart ready service 36 | Service à potentiel d'intelligence défini par l'utilisateur 36 | Benutzerdefinierter Smart-Ready-Dienst 36
| 1101 | User defined smart ready service 37 | User defined smart ready service 37 | Service à potentiel d'intelligence défini par l'utilisateur 37 | Benutzerdefinierter Smart-Ready-Dienst 37
| 1102 | User defined smart ready service 38 | User defined smart ready service 38 | Service à potentiel d'intelligence défini par l'utilisateur 38 | Benutzerdefinierter Smart-Ready-Dienst 38
| 1103 | User defined smart ready service 39 | User defined smart ready service 39 | Service à potentiel d'intelligence défini par l'utilisateur 39 | Benutzerdefinierter Smart-Ready-Dienst 39
| 1104 | User defined smart ready service 40 | User defined smart ready service 40 | Service à potentiel d'intelligence défini par l'utilisateur 40 | Benutzerdefinierter Smart-Ready-Dienst 40
| 1105 | User defined smart ready service 41 | User defined smart ready service 41 | Service à potentiel d'intelligence défini par l'utilisateur 41 | Benutzerdefinierter Smart-Ready-Dienst 41
| 1106 | User defined smart ready service 42 | User defined smart ready service 42 | Service à potentiel d'intelligence défini par l'utilisateur 42 | Benutzerdefinierter Smart-Ready-Dienst 42
| 1107 | User defined smart ready service 43 | User defined smart ready service 43 | Service à potentiel d'intelligence défini par l'utilisateur 43 | Benutzerdefinierter Smart-Ready-Dienst 43
| 1108 | User defined smart ready service 44 | User defined smart ready service 44 | Service à potentiel d'intelligence défini par l'utilisateur 44 | Benutzerdefinierter Smart-Ready-Dienst 44
| 1109 | User defined smart ready service 45 | User defined smart ready service 45 | Service à potentiel d'intelligence défini par l'utilisateur 45 | Benutzerdefinierter Smart-Ready-Dienst 45
| 1110 | User defined level 1-0 | User defined level 1-0 | Niveau défini par l'utilisateur 1-0 | Benutzerdefinierte Stufe 1-0
| 1111 | User defined level 1-1 | User defined level 1-1 | Niveau défini par l'utilisateur 1-1 | Benutzerdefinierte Ebene 1-1
| 1112 | User defined level 1-2 | User defined level 1-2 | Niveau défini par l'utilisateur 1-2 | Benutzerdefinierte Stufe 1-2
| 1113 | User defined level 1-3 | User defined level 1-3 | Niveau défini par l'utilisateur 1-3 | Benutzerdefinierte Stufe 1-3
| 1114 | User defined level 1-4 | User defined level 1-4 | Niveau défini par l'utilisateur 1-4 | Benutzerdefinierte Stufe 1-4
| 1115 | Please define your preconditions for this service | Please define your preconditions for this service | Veuillez définir les préconditions pour ce service | Bitte definieren Sie Ihre Voraussetzungen für diesen Dienst
| 1116 | 0
| 1117 | ASSESSMENT DATE | ASSESSMENT DATE | DATE DE L'EVALUATION | BEWERTUNGSDATUM
| 1118 | Year | Year | Année | Jahr
| 1119 | Month | Month | Mois | Monat
| 1120 | Day | Day | Jour | Tag
| 1121 | 1 | 1 | 1 | 1
| 1122 | 2 | 2 | 2 | 2
| 1123 | 3 | 3 | 3 | 3
| 1124 | 4 | 4 | 4 | 4
| 1125 | 5 | 5 | 5 | 5
| 1126 | 6 | 6 | 6 | 6
| 1127 | 7 | 7 | 7 | 7
| 1128 | 8 | 8 | 8 | 8
| 1129 | 9 | 9 | 9 | 9
| 1130 | 10 | 10 | 10 | 10
| 1131 | 11 | 11 | 11 | 11
| 1132 | 12 | 12 | 12 | 12
| 1133 | 1 | 1 | 1 | 1
| 1134 | 2 | 2 | 2 | 2
| 1135 | 3 | 3 | 3 | 3
| 1136 | 4 | 4 | 4 | 4
| 1137 | 5 | 5 | 5 | 5
| 1138 | 6 | 6 | 6 | 6
| 1139 | 7 | 7 | 7 | 7
| 1140 | 8 | 8 | 8 | 8
| 1141 | 9 | 9 | 9 | 9
| 1142 | 10 | 10 | 10 | 10
| 1143 | 11 | 11 | 11 | 11
| 1144 | 12 | 12 | 12 | 12
| 1145 | 13 | 13 | 13 | 13
| 1146 | 14 | 14 | 14 | 14
| 1147 | 15 | 15 | 15 | 15
| 1148 | 16 | 16 | 16 | 16
| 1149 | 17 | 17 | 17 | 17
| 1150 | 18 | 18 | 18 | 18
| 1151 | 19 | 19 | 19 | 19
| 1152 | 20 | 20 | 20 | 20
| 1153 | 21 | 21 | 21 | 21
| 1154 | 22 | 22 | 22 | 22
| 1155 | 23 | 23 | 23 | 23
| 1156 | 24 | 24 | 24 | 24
| 1157 | 25 | 25 | 25 | 25
| 1158 | 26 | 26 | 26 | 26
| 1159 | 27 | 27 | 27 | 27
| 1160 | 28 | 28 | 28 | 28
| 1161 | 29 | 29 | 29 | 29
| 1162 | 30 | 30 | 30 | 30
| 1163 | 31 | 31 | 31 | 31
| 1164 | 2020 | 2020 | 2020 | 2020
| 1165 | 2021 | 2021 | 2021 | 2021
| 1166 | 2022 | 2022 | 2022 | 2022
| 1167 | 2023 | 2023 | 2023 | 2023
| 1168 | 2024 | 2024 | 2024 | 2024
| 1169 | 0
| 1170 | 0
| 1171 | 0
| 1172 | 0
| 1173 | 0
| 1174 | 0
| 1175 | 0
| 1176 | 0
| 1177 | 0
| 1178 | 0
| 1179 | 0
| 1180 | 0
| 1181 | 0
| 1182 | 0
| 1183 | 0
| 1184 | 0
| 1185 | 0
| 1186 | 0
| 1187 | 0
| 1188 | 0
| 1189 | 0
| 1190 | 0
| 1191 | 0
| 1192 | 0
| 1193 | 0
| 1194 | 0
| 1195 | 0
| 1196 | 0
| 1197 | 0
| 1198 | 0
| 1199 | 0
| 1200 | 0
| 1201 | 0
| 1202 | 0
| 1203 | 0
| 1204 | 0
| 1205 | 0
| 1206 | 0
| 1207 | 0
| 1208 | 0
| 1209 | 0
| 1210 | 0
| 1211 | 0
| 1212 | 0
| 1213 | 0
| 1214 | 0
| 1215 | 0
| 1216 | 0
| 1217 | 0
| 1218 | 0
| 1219 | 0
| 1220 | 0
| 1221 | 0
| 1222 | 0
| 1223 | 0
| 1224 | 0
| 1225 | 0
| 1226 | 0
| 1227 | 0
| 1228 | 0
| 1229 | 0
| 1230 | 0
| 1231 | 0
| 1232 | 0
| 1233 | 0
| 1234 | 0
| 1235 | 0
| 1236 | 0
| 1237 | 0
| 1238 | 0
| 1239 | 0
| 1240 | 0
| 1241 | 0
| 1242 | 0
| 1243 | 0
| 1244 | 0
| 1245 | 0
| 1246 | 0
| 1247 | 0
| 1248 | 0
| 1249 | 0
| 1250 | 0
| 1251 | 0
| 1252 | 0
| 1253 | 0
| 1254 | 0
| 1255 | 0
| 1256 | 0
| 1257 | 0
| 1258 | 0
| 1259 | 0
| 1260 | 0
| 1261 | 0
| 1262 | 0
| 1263 | 0
| 1264 | 0
| 1265 | 0
| 1266 | 0
| 1267 | 0
| 1268 | 0
| 1269 | 0
| 1270 | 0
| 1271 | 0
| 1272 | 0
| 1273 | 0
| 1274 | 0
| 1275 | 0
| 1276 | 0
| 1277 | 0
| 1278 | 0
| 1279 | 0
| 1280 | 0
| 1281 | 0
| 1282 | 0
| 1283 | 0
| 1284 | 0
| 1285 | 0
| 1286 | 0
| 1287 | 0
| 1288 | 0
| 1289 | 0
| 1290 | 0
| 1291 | 0
| 1292 | 0
| 1293 | 0
| 1294 | 0
| 1295 | 0
| 1296 | 0
| 1297 | 0
| 1298 | 0
| 1299 | 0
| 1300 | 0
| 1301 | 0
| 1302 | 0
| 1303 | 0
| 1304 | 0
| 1305 | 0
| 1306 | 0
| 1307 | 0
| 1308 | 0
| 1309 | 0
| 1310 | 0
| 1311 | 0
| 1312 | 0
| 1313 | 0
| 1314 | 0
| 1315 | 0
| 1316 | 0
| 1317 | 0
| 1318 | 0
| 1319 | 0
| 1320 | 0
| 1321 | 0
| 1322 | 0
| 1323 | 0
| 1324 | 0
| 1325 | 0
| 1326 | 0
| 1327 | 0
| 1328 | 0
| 1329 | 0
| 1330 | 0
| 1331 | 0
| 1332 | 0
| 1333 | 0
| 1334 | 0
| 1335 | 0
| 1336 | 0
| 1337 | 0
| 1338 | 0
| 1339 | 0
| 1340 | 0
| 1341 | 0
| 1342 | 0
| 1343 | 0
| 1344 | 0
| 1345 | 0
| 1346 | 0
| 1347 | 0
| 1348 | 0
| 1349 | 0
| 1350 | 0
| 1351 | 0
| 1352 | 0
| 1353 | 0
| 1354 | 0
| 1355 | 0
| 1356 | 0
| 1357 | 0
| 1358 | 0
| 1359 | 0
| 1360 | 0
| 1361 | 0
| 1362 | 0
| 1363 | 0
| 1364 | 0
| 1365 | 0
| 1366 | 0
| 1367 | 0
| 1368 | 0
| 1369 | 0
| 1370 | 0
| 1371 | 0
| 1372 | 0
| 1373 | 0
| 1374 | 0
| 1375 | 0
| 1376 | 0
| 1377 | 0
| 1378 | 0
| 1379 | 0
| 1380 | 0
| 1381 | 0
| 1382 | 0
| 1383 | 0
| 1384 | 0
| 1385 | 0
| 1386 | 0
| 1387 | 0
| 1388 | 0
| 1389 | 0
| 1390 | 0
| 1391 | 0
| 1392 | 0
| 1393 | 0
| 1394 | 0
| 1395 | 0
| 1396 | 0
| 1397 | 0
| 1398 | 0
| 1399 | 0
| 1400 | 0
| 1401 | 0
| 1402 | 0
| 1403 | 0
| 1404 | 0
| 1405 | 0
| 1406 | 0
| 1407 | 0
| 1408 | 0
| 1409 | 0
| 1410 | 0
| 1411 | 0
| 1412 | 0
| 1413 | 0
| 1414 | 0
| 1415 | 0
| 1416 | 0
| 1417 | 0
| 1418 | 0
| 1419 | 0
| 1420 | 0
| 1421 | 0
| 1422 | 0
| 1423 | 0
| 1424 | 0
| 1425 | 0
| 1426 | 0
| 1427 | 0
| 1428 | 0
| 1429 | 0
| 1430 | 0
| 1431 | 0
| 1432 | 0
| 1433 | 0
| 1434 | 0
| 1435 | 0
| 1436 | 0
| 1437 | 0
| 1438 | 0
| 1439 | 0
| 1440 | 0
| 1441 | 0
| 1442 | 0
| 1443 | 0
| 1444 | 0
| 1445 | 0
| 1446 | 0
| 1447 | 0
| 1448 | 0
| 1449 | 0
| 1450 | 0
| 1451 | 0
| 1452 | 0
| 1453 | 0
| 1454 | 0
| 1455 | 0
| 1456 | 0
| 1457 | 0
| 1458 | 0
| 1459 | 0
| 1460 | 0
| 1461 | 0
| 1462 | 0
| 1463 | 0
| 1464 | 0
| 1465 | 0
| 1466 | 0
| 1467 | 0
| 1468 | 0
| 1469 | 0
| 1470 | 0
| 1471 | 0
| 1472 | 0
| 1473 | 0
| 1474 | 0
| 1475 | 0
| 1476 | 0
| 1477 | 0
| 1478 | 0
| 1479 | 0
| 1480 | 0
| 1481 | 0
| 1482 | 0
| 1483 | 0
| 1484 | 0
| 1485 | 0
| 1486 | 0
| 1487 | 0
| 1488 | 0
| 1489 | 0
| 1490 | 0
| 1491 | 0
| 1492 | 0
| 1493 | 0
| 1494 | 0
| 1495 | 0
| 1496 | 0
| 1497 | 0
| 1498 | 0
| 1499 | 0
| 1500 | 0
| 1501 | 0
| 1502 | 0
| 1503 | 0
| 1504 | 0
| 1505 | 0
| 1506 | 0
| 1507 | 0
| 1508 | 0
| 1509 | 0
| 1510 | 0
| 1511 | 0
| 1512 | 0
| 1513 | 0
| 1514 | 0
| 1515 | 0
| 1516 | 0
| 1517 | 0
| 1518 | 0
| 1519 | 0
| 1520 | 0
| 1521 | 0
| 1522 | 0
| 1523 | 0
| 1524 | 0
| 1525 | 0
| 1526 | 0
| 1527 | 0
| 1528 | 0
| 1529 | 0
| 1530 | 0
| 1531 | 0
| 1532 | 0
| 1533 | 0
| 1534 | 0
| 1535 | 0
| 1536 | 0
| 1537 | 0
| 1538 | 0
| 1539 | 0
| 1540 | 0
| 1541 | 0
| 1542 | 0
| 1543 | 0
| 1544 | 0
| 1545 | 0
| 1546 | 0
| 1547 | 0
| 1548 | 0
| 1549 | 0
| 1550 | 0
| 1551 | 0
| 1552 | 0
| 1553 | 0
| 1554 | 0
| 1555 | 0
| 1556 | 0
| 1557 | 0
| 1558 | 0
| 1559 | 0
| 1560 | 0
| 1561 | 0
| 1562 | 0
| 1563 | 0
| 1564 | 0
| 1565 | 0
| 1566 | 0
| 1567 | 0
| 1568 | 0
| 1569 | 0
| 1570 | 0
| 1571 | 0
| 1572 | 0
| 1573 | 0
| 1574 | 0
| 1575 | 0
| 1576 | 0
| 1577 | 0
| 1578 | 0
| 1579 | 0
| 1580 | 0
| 1581 | 0
| 1582 | 0
| 1583 | 0
| 1584 | 0
| 1585 | 0
| 1586 | 0
| 1587 | 0
| 1588 | 0
| 1589 | 0
| 1590 | 0
| 1591 | 0
| 1592 | 0
| 1593 | 0
| 1594 | 0
| 1595 | 0
| 1596 | 0
| 1597 | 0
| 1598 | 0
| 1599 | 0
| 1600 | 0
| 1601 | 0
| 1602 | 0
| 1603 | 0
| 1604 | 0
| 1605 | 0
| 1606 | 0
| 1607 | 0
| 1608 | 0
| 1609 | 0
| 1610 | 0
| 1611 | 0
| 1612 | 0
| 1613 | 0
| 1614 | 0
| 1615 | 0
| 1616 | 0
| 1617 | 0
| 1618 | 0
| 1619 | 0
| 1620 | 0
| 1621 | 0
| 1622 | 0
| 1623 | 0
| 1624 | 0
| 1625 | 0
| 1626 | 0
| 1627 | 0
| 1628 | 0
| 1629 | 0
| 1630 | 0
| 1631 | 0
| 1632 | 0
| 1633 | 0
| 1634 | 0
| 1635 | 0
| 1636 | 0
| 1637 | 0
| 1638 | 0
| 1639 | 0
| 1640 | 0
| 1641 | 0
| 1642 | 0
| 1643 | 0
| 1644 | 0
| 1645 | 0
| 1646 | 0
| 1647 | 0
| 1648 | 0
| 1649 | 0
| 1650 | 0
| 1651 | 0
| 1652 | 0
| 1653 | 0
| 1654 | 0
| 1655 | 0
| 1656 | 0
| 1657 | 0
| 1658 | 0
| 1659 | 0
| 1660 | 0
| 1661 | 0
| 1662 | 0
| 1663 | 0
| 1664 | 0
| 1665 | 0
| 1666 | 0
| 1667 | 0
| 1668 | 0
| 1669 | 0
| 1670 | 0
| 1671 | 0
| 1672 | 0
| 1673 | 0
| 1674 | 0
| 1675 | 0
| 1676 | 0
| 1677 | 0
| 1678 | 0
| 1679 | 0
| 1680 | 0
| 1681 | 0
| 1682 | 0
| 1683 | 0
| 1684 | 0
| 1685 | 0
| 1686 | 0
| 1687 | 0
| 1688 | 0
| 1689 | 0
| 1690 | 0
| 1691 | 0
| 1692 | 0
| 1693 | 0
| 1694 | 0
| 1695 | 0
| 1696 | 0
| 1697 | 0
| 1698 | 0
| 1699 | 0
| 1700 | 0
| 1701 | 0
| 1702 | 0
| 1703 | 0
| 1704 | 0
| 1705 | 0
| 1706 | 0
| 1707 | 0
| 1708 | 0
| 1709 | 0
| 1710 | 0
| 1711 | 0
| 1712 | 0
| 1713 | 0
| 1714 | 0
| 1715 | 0
| 1716 | 0
| 1717 | 0
| 1718 | 0
| 1719 | 0
| 1720 | 0
| 1721 | 0
| 1722 | 0
| 1723 | 0
| 1724 | 0
| 1725 | 0
| 1726 | 0
| 1727 | 0
| 1728 | 0
| 1729 | 0
| 1730 | 0
| 1731 | 0
| 1732 | 0
| 1733 | 0
| 1734 | 0
| 1735 | 0
| 1736 | 0
| 1737 | 0
| 1738 | 0
| 1739 | 0
| 1740 | 0
| 1741 | 0
| 1742 | 0
| 1743 | 0
| 1744 | 0
| 1745 | 0
| 1746 | 0
| 1747 | 0
| 1748 | 0
| 1749 | 0
| 1750 | 0
| 1751 | 0
| 1752 | 0
| 1753 | 0
| 1754 | 0
| 1755 | 0
| 1756 | 0
| 1757 | 0
| 1758 | 0
| 1759 | 0
| 1760 | 0
| 1761 | 0
| 1762 | 0
| 1763 | 0
| 1764 | 0
| 1765 | 0
| 1766 | 0
| 1767 | 0
| 1768 | 0
| 1769 | 0
| 1770 | 0
| 1771 | 0
| 1772 | 0
| 1773 | 0
| 1774 | 0
| 1775 | 0
| 1776 | 0
| 1777 | 0
| 1778 | 0
| 1779 | 0
| 1780 | 0
| 1781 | 0
| 1782 | 0
| 1783 | 0
| 1784 | 0
| 1785 | 0
| 1786 | 0
| 1787 | 0
| 1788 | 0
| 1789 | 0
| 1790 | 0
| 1791 | 0
| 1792 | 0
| 1793 | 0
| 1794 | 0
| 1795 | 0
| 1796 | 0
| 1797 | 0
| 1798 | 0
| 1799 | 0
| 1800 | 0
| 1801 | 0
| 1802 | 0
| 1803 | 0
| 1804 | 0
| 1805 | 0
| 1806 | 0
| 1807 | 0
| 1808 | 0
| 1809 | 0
| 1810 | 0
| 1811 | 0
| 1812 | 0
| 1813 | 0
| 1814 | 0
| 1815 | 0
| 1816 | 0
| 1817 | 0
| 1818 | 0
| 1819 | 0
| 1820 | 0
| 1821 | 0
| 1822 | 0
| 1823 | 0
| 1824 | 0
| 1825 | 0
| 1826 | 0
| 1827 | 0
| 1828 | 0
| 1829 | 0
| 1830 | 0
| 1831 | 0
| 1832 | 0
| 1833 | 0
| 1834 | 0
| 1835 | 0
| 1836 | 0
| 1837 | 0
| 1838 | 0
| 1839 | 0
| 1840 | 0
| 1841 | 0
| 1842 | 0
| 1843 | 0
| 1844 | 0
| 1845 | 0
| 1846 | 0
| 1847 | 0
| 1848 | 0
| 1849 | 0
| 1850 | 0
| 1851 | 0
| 1852 | 0
| 1853 | 0
| 1854 | 0
| 1855 | 0
| 1856 | 0
| 1857 | 0
| 1858 | 0
| 1859 | 0
| 1860 | 0
| 1861 | 0
| 1862 | 0
| 1863 | 0
| 1864 | 0
| 1865 | 0
| 1866 | 0
| 1867 | 0
| 1868 | 0
| 1869 | 0
| 1870 | 0
| 1871 | 0
| 1872 | 0
| 1873 | 0
| 1874 | 0
| 1875 | 0
| 1876 | 0
| 1877 | 0
| 1878 | 0
| 1879 | 0
| 1880 | 0
| 1881 | 0
| 1882 | 0
| 1883 | 0
| 1884 | 0
| 1885 | 0
| 1886 | 0
| 1887 | 0
| 1888 | 0
| 1889 | 0
| 1890 | 0
| 1891 | 0
| 1892 | 0
| 1893 | 0
| 1894 | 0
| 1895 | 0
| 1896 | 0
| 1897 | 0
| 1898 | 0
| 1899 | 0
| 1900 | 0
| 1901 | 0
| 1902 | 0
| 1903 | 0
| 1904 | 0
| 1905 | 0
| 1906 | 0
| 1907 | 0
| 1908 | 0
| 1909 | 0
| 1910 | 0
| 1911 | 0
| 1912 | 0
| 1913 | 0
| 1914 | 0
| 1915 | 0
| 1916 | 0
| 1917 | 0
| 1918 | 0
| 1919 | 0
| 1920 | 0
| 1921 | 0
| 1922 | 0
| 1923 | 0
| 1924 | 0
| 1925 | 0
| 1926 | 0
| 1927 | 0
| 1928 | 0
| 1929 | 0
| 1930 | 0
| 1931 | 0
| 1932 | 0
| 1933 | 0
| 1934 | 0
| 1935 | 0
| 1936 | 0
| 1937 | 0
| 1938 | 0
| 1939 | 0
| 1940 | 0
| 1941 | 0
| 1942 | 0
| 1943 | 0
| 1944 | 0
| 1945 | 0
| 1946 | 0
| 1947 | 0
| 1948 | 0
| 1949 | 0
| 1950 | 0
| 1951 | 0
| 1952 | 0
| 1953 | 0
| 1954 | 0
| 1955 | 0
| 1956 | 0
| 1957 | 0
| 1958 | 0
| 1959 | 0
| 1960 | 0
| 1961 | 0
| 1962 | 0
| 1963 | 0
| 1964 | 0
| 1965 | 0
| 1966 | 0
| 1967 | 0
| 1968 | 0
| 1969 | 0
| 1970 | 0
| 1971 | 0
| 1972 | 0
| 1973 | 0
| 1974 | 0
| 1975 | 0
| 1976 | 0
| 1977 | 0
| 1978 | 0
| 1979 | 0
| 1980 | 0
| 1981 | 0
| 1982 | 0
| 1983 | 0
| 1984 | 0
| 1985 | 0
| 1986 | 0
| 1987 | 0
| 1988 | 0
| 1989 | 0
| 1990 | 0
| 1991 | 0
| 1992 | 0
| 1993 | 0
| 1994 | 0
| 1995 | 0
| 1996 | 0
| 1997 | 0
| 1998 | 0
| 1999 | 0
| 2000 | 0
| 2001 | 0
| 2002 | 0
| 2003 | 0
| 2004 | 0
| 2005 | 0
| 2006 | 0
| 2007 | 0
| 2008 | 0
| 2009 | 0
| 2010 | 0
| 2011 | 0
| 2012 | 0
| 2013 | 0
| 2014 | 0
| 2015 | 0
| 2016 | 0
| 2017 | 0
| 2018 | 0
| 2019 | 0
| 2020 | 0
| 2021 | 0
| 2022 | 0
Note on D52: Ma Yixiao: no need to translate row 52 - 105
Note on H1: Ma Yixiao: more languages in the same structure

## Calculation
[30 empty] | ORDINAL IMPACT SCORES - main functionality | [7 empty] | ORDINAL IMPACT SCORES - additional functionality | [8 empty] | Impact weightings by domain | [6 empty] | SRI impact scores by domain | [6 empty] | SRI impact scores by domain - additional functionality | [6 empty] | SRI impact scores by domain - Combined for whole building | [7 empty] | SRI impact scores by domain after impact weightings also applied | [9 empty] | MAXIMUM POSSIBLE ORDINAL IMPACT SCORES | [6 empty] | Maximum possible SRI impact scores by domain | [7 empty] | Maximum possible SRI impact scores by domain after impact weightings also applied | [7 empty] | Normalised SRI impact scores by domain after impact weightings also applied
|  | building type --> | non-residential | Preferred services catalogue |  |  | B | [5 empty] | 0 | 0 | 1 | 2 | 3 | 4 | [9 empty] | 14 | 12 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 22 | 23 | 24 | 25 | 26 | 27 | 28 | [7 empty] | 18 | 19 | 20 | 21 | 22 | 23 | 24 | [8 empty] | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | [8 empty] | 22 | 23 | 24 | 25 | 26 | 27 | 28 | [9 empty] | Step (b) in Regulation: for each impact criterion, the (ordinal) score I(d,ic) of each technical domain is | [6 empty] | Step (c) in Regulation: the maximum (ordinal) score of each technical domain for each impact criterion Imax(d,ic) is | [6 empty] | Step (d) in Regulation: score for each impact criterion | [6 empty] | Step (e) in Regulation: scores for each key functionality |  |  | Step (f) in Regulation | Step (g) in Regulation: scores of each technical domain and impact criterion | [6 empty] | Domains scores (not in the Regulation) | SRI score
Domain | Code | Service group | Smart ready service | Service included in the selected method (A/B/custom): 0 - not included, 1 - included | 1 - This domain is present; 2 - This domain is absent but mandatory; 0 - This domain is absent and not mandatory | TRIAGE: 1 - This service affects maximum obtainable score, even if service is not applicable in this building; 0 - This service does not affect maximum obtainable score when not present in building |  | Service applicable in your building? - to be assessed by the assessor: 1 - applicable; 0 - not applicable | Main functionality level as inspected by SRI assessor | share (default = 100% means applicable throughout the building) | Optional: additional functionality level in part of the building | Share of additional functionality level | Warnings | Functionality level 0 (as non-smart default) | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4 | Service part of the method and domain selection? | Service applicable? | Optional feedback: Estimated assessment time (minutes) | Optional: assessor's comments | Included in max. score? | Resulting main functionality level for this building | Resulting additional functionality level for this building | Max possible functionality level | Max functionality level in this building | tab | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | tab | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Total |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Total | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | (1) energy performance and operation | (2) response to the needs of the occupants | (3) energy flexibility | SRI score | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  | 32.78%
Totals | [28 empty] | 4 | 29 | 8 | 18 | 16 | 10 | 8 | 17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | South Europe | [6 empty] | 5.239 | 1.9973 | 2.92 | 2 | 1.64 | 1.1689 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.87317 | 0.66575 | 0.24333 | 0.16667 | 0.13667 | 0.19481 | 0.18333 | 2.4637 |  |  | 79 | 45 | 36 | 60 | 22 | 29 | 30 | 12.2798 | 9.2428 | 5.88 | 7.7 | 3.68 | 4.7737 | 4.2 |  | 2.0466 | 3.0809 | 0.49 | 0.64167 | 0.30667 | 0.79561 | 0.35 | 7.7115 | 42.66% | 21.61% | 49.66% | 25.97% | 44.57% | 24.49% | 52.38% | Heating | 3.6237 | 0.83492 | 0.96 | 0.3 | 0.32 | 0.35938 | 0.22857 | 5.7376 | 4.5921 | 1.6 | 0.8 | 0.48 | 1.4375 | 0.34286 | 42.66% | 21.61% | 49.66% | 25.97% | 44.57% | 24.49% | 52.38% | 33.57% | 43.15% | 21.61% | 32.78% | 63.16% | 18.18% | 60% | 37.5% | 66.67% | 25% | 66.67%
[76 empty] | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | [33 empty] | Domestic hot water | 0.10727 | 0 | 0 | 0 | 0 | 0.12766 | 0.22857 | 0.53636 | 0.88977 | 0 | 0.5 | 0 | 0.25532 | 0.34286 | 0.5 | 1 | 0.25 | 0.25 | 0.25 | 0.5 | 0.25 | 0.33333 | 0.33333 | 0.33333 |  | 20% | 0% | #DIV/0! | 0% | #DIV/0! | 50% | 66.67%
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | No automatic control | Central automatic control (e.g. central thermostat) | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | H | 10 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.60395 | 0 | 0.32 | 0.2 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0 | 0.32 | 0.2 | 0.32 | 0 | 0 | 67 | 0.10066 | 0 | 0.026667 | 0.016667 | 0.026667 | 0 | 0 |  | H | 12 | 3 | 0 | 2 | 3 | 2 | 1 | 0 | 0.90593 | 0 | 0.32 | 0.3 | 0.32 | 0.35938 | 0 | 67 | 0.15099 | 0 | 0.026667 | 0.025 | 0.026667 | 0.059896 | 0 | [8 empty] | Cooling | 0.82203 | 0.16234 | 0.64 | 0.4 | 0.32 | 0.13975 | 0.22857 | 2.3486 | 1.7857 | 1.28 | 0.8 | 0.48 | 0.55901 | 0.34286 | [11 empty] | 35% | 9.091% | 50% | 50% | 66.67% | 25% | 66.67%
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 1 | 1 | 0 |  | 0 | 3 | 100% |  | 0% |  | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 3 | 0 | H | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Ventilation | 0.43844 | 0 | 1.12 | 0.5 | 0.8 | 0.10435 | 0.11429 | 1.2276 | 0 | 1.6 | 0.8 | 1.44 | 0.20871 | 0.34286 | [11 empty] | 35.71% | #DIV/0! | 70% | 62.5% | 55.56% | 50% | 33.33%
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | No automatic control | Outside temperature compensated control | Demand based control | 0 | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 2 | 2 | H | 40 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.30198 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30198 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 67 | 0.05033 | 0 | 0.013333 | 0.0083333 | 0 | 0 | 0 |  | H | 41 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0.60395 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 67 | 0.10066 | 0 | 0.013333 | 0.0083333 | 0 | 0 | 0 | [8 empty] | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71872 | 0 | 0.8 | 0.5 | 0.48 | 0 | 0 | [11 empty] | 0% | #DIV/0! | 0% | 0% | 0% | #DIV/0! | #DIV/0!
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 1 | 1 | 0 |  | 1 | 3 | 100% |  | 0% |  | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 1 | 1 |  |  | 1 | 3 | 0 | 4 | 4 | H | 56 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.60395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 57 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Dynamic building envelope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Heat storage capable of flexible control through grid signals (e.g. DSM) | 0 | 1 | 1 |  |  | 1 | 2 | 0 | 3 | 3 | H | 70 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.60395 | 0.41746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0.41746 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0.13915 | 0 | 0 | 0 | 0 | 0 |  | H | 71 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0.83492 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0.27831 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Electricity | 0.047534 | 0 | 0 | 0 | 0 | 0.037712 | 0.8 | 0.11091 | 0.17523 | 0 | 0.9 | 0 | 0.11314 | 1.0286 | [11 empty] | 42.86% | 0% | #DIV/0! | 0% | #DIV/0! | 33.33% | 77.78%
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | 0 | 0 | 1 | 1 |  |  | 1 | 2 | 0 | 2 | 2 | H | 86 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.60395 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60395 | 0 | 0.32 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0 | 0.026667 | 0 | 0 | 0 | 0 |  | H | 86 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0.60395 | 0 | 0.32 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0 | 0.026667 | 0 | 0 | 0 | 0 | [8 empty] | Electric vehicle charging | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | On/Off-control of heat generator | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of heat generator capacity depending on the load AND external signals from grid | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | H | 99 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.30198 | 0.41746 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30198 | 0.41746 | 0.16 | 0 | 0 | 0 | 0 | 67 | 0.05033 | 0.13915 | 0.013333 | 0 | 0 | 0 | 0 |  | H | 101 | 2 | 3 | 2 | 0 | 0 | 0 | 0 | 0.60395 | 1.2524 | 0.32 | 0 | 0 | 0 | 0 | 67 | 0.10066 | 0.41746 | 0.026667 | 0 | 0 | 0 | 0 | [8 empty] | Monitoring and control | 0.2 | 1 | 0.2 | 0.8 | 0.2 | 0.4 | 0.6 | 1.6 | 1.8 | 0.6 | 3.4 | 0.8 | 2.2 | 1.8 | [11 empty] | 12.5% | 55.56% | 33.33% | 23.53% | 25% | 18.18% | 33.33%
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 1 | 1 |  |  | 1 | 1 | 0 | 4 | 4 | H | 114 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.30198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30198 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.05033 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 117 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0.90593 | 1.2524 | 0 | 0 | 0 | 0 | 0 | 67 | 0.15099 | 0.41746 | 0 | 0 | 0 | 0 | 0
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 | 1 |  | 1 | 2 | 100% |  | 0% |  | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | H | 131 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0.30198 | 0 | 0 | 0 | 0 | 0.35938 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30198 | 0 | 0 | 0 | 0 | 0.35938 | 0.22857 | 67 | 0.05033 | 0 | 0 | 0 | 0 | 0.059896 | 0.019048 |  | H | 133 | 1 | 0 | 0 | 1 | 0 | 3 | 3 | 0.30198 | 0 | 0 | 0.1 | 0 | 1.0781 | 0.34286 | 67 | 0.05033 | 0 | 0 | 0.0083333 | 0 | 0.17969 | 0.028571
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 | 1 |  | 0 | 4 | 100% |  | 0% |  | No automatic control | Scheduled operation of heating system | Self-learning optimal control of heating system | Heating system capable of flexible control through grid signals (e.g. DSM) | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | 1 | 0 |  |  | 1 | 0 | 0 | 4 | 4 | H | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 147 | 2 | 3 | 3 | 3 | 1 | 0 | 0 | 0.60395 | 1.2524 | 0.48 | 0.3 | 0.16 | 0 | 0 | 67 | 0.10066 | 0.41746 | 0.04 | 0.025 | 0.013333 | 0 | 0
Heating | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | DHW | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 11 | 2 | 3 | 0 | 2 | 0 | 0 | 0 | 0.21454 | 0.44489 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0.035757 | 0.1483 | 0 | 0.016667 | 0 | 0 | 0
Heating | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | DHW | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 25 | 2 | 3 | 0 | 2 | 0 | 0 | 0 | 0.21454 | 0.44489 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0.035757 | 0.1483 | 0 | 0.016667 | 0 | 0 | 0
| DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 1 | 1 | 0 |  | 0 | 3 | 100% |  | 0% |  | Manual selected control of solar energy or heat generation | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 3 | 0 | DHW | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 1 | 1 | 0 |  | 0 | 4 | 100% |  | 0% |  | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 1 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 | 1 |  | 1 | 2 | 100% |  | 0% |  | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | DHW | 69 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0.10727 | 0 | 0 | 0 | 0 | 0.12766 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10727 | 0 | 0 | 0 | 0 | 0.12766 | 0.22857 | 67 | 0.017879 | 0 | 0 | 0 | 0 | 0.021277 | 0.019048 |  | DHW | 71 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.10727 | 0 | 0 | 0.1 | 0 | 0.25532 | 0.34286 | 67 | 0.017879 | 0 | 0 | 0.0083333 | 0 | 0.042554 | 0.028571
Domestic hot water | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | No automatic control | Central automatic control | Individual room control | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | C | 10 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.11743 | 0 | 0.16 | 0.2 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11743 | 0 | 0.16 | 0.2 | 0.32 | 0 | 0 | 67 | 0.019572 | 0 | 0.013333 | 0.016667 | 0.026667 | 0 | 0 |  | C | 12 | 3 | 0 | 2 | 3 | 2 | 1 | 0 | 0.3523 | 0 | 0.32 | 0.3 | 0.32 | 0.13975 | 0 | 67 | 0.058716 | 0 | 0.026667 | 0.025 | 0.026667 | 0.023292 | 0
Domestic hot water | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 1 | 1 | 0 |  | 0 | 3 | 100% |  | 0% |  | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 3 | 0 | C | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | Constant temperature control | Outside temperature compensated control | Demand based control | 0 | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 2 | 2 | C | 37 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.11743 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11743 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 67 | 0.019572 | 0 | 0.013333 | 0.0083333 | 0 | 0 | 0 |  | C | 38 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0.23486 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 67 | 0.039144 | 0 | 0.013333 | 0.0083333 | 0 | 0 | 0
| C-1d | Cooling control - demand side | Control of distribution pumps in networks | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | C | 52 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.23486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23486 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.039144 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23486 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.039144 | 0 | 0 | 0 | 0 | 0 | 0
| C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 1 | 1 | 1 |  | 1 | 0 | 100% |  | 0% |  | No interlock | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Total interlock (control system ensures no simultaneous heating and cooling can take place) | 0 | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 2 | 2 | C | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 78 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.058716 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Cold storage capable of flexible control through grid signals (e.g. DSM) | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | C | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 93 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23486 | 0.32468 | 0 | 0 | 0 | 0 | 0 | 67 | 0.039144 | 0.10823 | 0 | 0 | 0 | 0 | 0
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | On/Off-control of cooling production | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of cooling production capacity depending on the load AND external signals from grid | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | C | 106 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.11743 | 0.16234 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11743 | 0.16234 | 0.16 | 0 | 0 | 0 | 0 | 67 | 0.019572 | 0.054114 | 0.013333 | 0 | 0 | 0 | 0 |  | C | 108 | 2 | 3 | 2 | 0 | 0 | 0 | 0 | 0.23486 | 0.48702 | 0.32 | 0 | 0 | 0 | 0 | 67 | 0.039144 | 0.16234 | 0.026667 | 0 | 0 | 0 | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | Priorities only based on running times | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Sequencing based on dynamic priority list, including external signals from grid | 1 | 1 |  |  | 1 | 0 | 0 | 4 | 4 | C | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 123 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0.3523 | 0.48702 | 0 | 0 | 0 | 0 | 0 | 67 | 0.058716 | 0.16234 | 0 | 0 | 0 | 0 | 0
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 | 1 |  | 1 | 2 | 100% |  | 0% |  | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | C | 135 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.11743 | 0 | 0 | 0 | 0 | 0.13975 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11743 | 0 | 0 | 0 | 0 | 0.13975 | 0.22857 | 67 | 0.019572 | 0 | 0 | 0 | 0 | 0.023292 | 0.019048 |  | C | 137 | 1 | 0 | 0 | 1 | 0 | 3 | 3 | 0.11743 | 0 | 0 | 0.1 | 0 | 0.41926 | 0.34286 | 67 | 0.019572 | 0 | 0 | 0.0083333 | 0 | 0.069876 | 0.028571
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | No automatic control | Scheduled operation of cooling system | Self-learning optimal control of cooling system | Cooling system capable of flexible control through grid signals (e.g. DSM) | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | 1 | 1 |  |  | 1 | 1 | 0 | 4 | 4 | C | 148 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0.11743 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11743 | 0 | 0.16 | 0.1 | 0 | 0 | 0 | 67 | 0.019572 | 0 | 0.013333 | 0.0083333 | 0 | 0 | 0 |  | C | 151 | 2 | 3 | 3 | 3 | 1 | 0 | 0 | 0.23486 | 0.48702 | 0.48 | 0.3 | 0.16 | 0 | 0 | 67 | 0.039144 | 0.16234 | 0.04 | 0.025 | 0.013333 | 0 | 0
Cooling | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | No ventilation system or manual control | Clock control | Occupancy detection control | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 1 | 1 |  |  | 1 | 1 | 0 | 4 | 4 | V | 9 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0.087687 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087687 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 | 67 | 0.014615 | 0 | 0.013333 | 0.0083333 | 0.013333 | 0 | 0 |  | V | 12 | 3 | 0 | 3 | 3 | 3 | 0 | 0 | 0.26306 | 0 | 0.48 | 0.3 | 0.48 | 0 | 0 | 67 | 0.043844 | 0 | 0.04 | 0.025 | 0.04 | 0 | 0
Cooling | V-1c | Air flow control | Air flow or pressure control at the air handler level | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | Multi-stage control: To reduce the auxiliary energy demand of the fan | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | 1 | 1 |  |  | 1 | 0 | 0 | 4 | 4 | V | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 28 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26306 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.043844 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | Without overheating control | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | 0 | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 2 | 2 | V | 42 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0.087687 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087687 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 | 67 | 0.014615 | 0 | 0.013333 | 0.0083333 | 0.013333 | 0 | 0 |  | V | 43 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 0.17537 | 0 | 0.32 | 0.2 | 0.32 | 0 | 0 | 67 | 0.029229 | 0 | 0.026667 | 0.016667 | 0.026667 | 0 | 0
| V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | No automatic control | Constant setpoint: A control loop enables to control the supply air_x000D_ temperature, the setpoint is constant and can only be modified by a manual_x000D_ action | Variable set point with outdoor temperature compensation | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | 0 | 1 | 1 |  |  | 1 | 2 | 0 | 3 | 3 | V | 57 | 2 | 0 | 2 | 1 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0.17537 | 0 | 0.32 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17537 | 0 | 0.32 | 0.1 | 0 | 0 | 0 | 67 | 0.029229 | 0 | 0.026667 | 0.0083333 | 0 | 0 | 0 |  | V | 58 | 3 | 0 | 2 | 1 | 0 | 0 | 0 | 0.26306 | 0 | 0.32 | 0.1 | 0 | 0 | 0 | 67 | 0.043844 | 0 | 0.026667 | 0.0083333 | 0 | 0 | 0
| V-3 | Free cooling | Free cooling with mechanical ventilation system | 1 | 1 | 0 |  | 1 | 1 | 100% |  | 0% |  | No automatic control | Night cooling | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical_x000D_ cooling | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | V | 70 | 1 | 0 | 3 | 2 | 1 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0.087687 | 0 | 0.48 | 0.2 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087687 | 0 | 0.48 | 0.2 | 0.16 | 0 | 0 | 67 | 0.014615 | 0 | 0.04 | 0.016667 | 0.013333 | 0 | 0 |  | V | 72 | 3 | 0 | 3 | 2 | 1 | 0 | 0 | 0.26306 | 0 | 0.48 | 0.2 | 0.16 | 0 | 0 | 67 | 0.043844 | 0 | 0.04 | 0.016667 | 0.013333 | 0 | 0
Mechanical ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | None | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | V | 96 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0.32 | 0.10435 | 0.11429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0.10435 | 0.11429 | 67 | 0 | 0 | 0 | 0 | 0.026667 | 0.017392 | 0.0095238 |  | V | 98 | 0 | 0 | 0 | 0 | 3 | 2 | 3 | 0 | 0 | 0 | 0 | 0.48 | 0.20871 | 0.34286 | 67 | 0 | 0 | 0 | 0 | 0.04 | 0.034785 | 0.028571
Mechanical ventilation | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 | 1 |  | 1 | 0 | 100% |  | 0% |  | Manual on/off switch | Manual on/off switch + additional sweeping extinction signal | Automatic detection (auto on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) | 0 | 1 | 1 |  | Modern LED lamps already installed. | 1 | 0 | 0 | 3 | 3 | L | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 11 | 3 | 0 | 2 | 2 | 0 | 0 | 0 | 0.35936 | 0 | 0.32 | 0.2 | 0 | 0 | 0 | 67 | 0.059893 | 0 | 0.026667 | 0.016667 | 0 | 0 | 0
Mechanical ventilation | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 1 | 1 | 1 |  | 1 | 0 | 100% |  | 0% |  | Manual (central) | Manual (per room / zone) | Automatic switching | Automatic dimming | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | 1 | 1 |  |  | 1 | 0 | 0 | 4 | 4 | L | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 28 | 3 | 0 | 3 | 3 | 3 | 0 | 0 | 0.35936 | 0 | 0.48 | 0.3 | 0.48 | 0 | 0 | 67 | 0.059893 | 0 | 0.04 | 0.025 | 0.04 | 0 | 0
Mechanical ventilation | DE-1 | Window control | Window solar shading control | 1 | 0 | 0 |  | 1 | 4 | 100% |  | 0% |  | No sun shading or only manual operation | Motorized operation with manual control | Motorized operation with automatic control based on sensor data | Combined light/blind/HVAC control | Predictive blind control (e.g. based on weather forecast) | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | DE-2 | Window control | Window open/closed control, combined with HVAC system | 1 | 0 | 1 |  | 1 | 3 | 100% |  | 0% |  | Manual operation or only fixed windows | Open/closed detection to shut down heating or cooling systems | Level 1 + Automised mechanical window opening based on room sensor data | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 3 | 0 | DE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 0 | 0 |  | 1 | 4 | 100% |  | 0% |  | No reporting | Position of each product & fault detection | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 | 0 |  | 1 | 3 | 100% |  | 0% |  | None | Current generation data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  |  | 1 | 3 | 0 | 4 | 4 | E | 12 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0.015845 | 0 | 0 | 0 | 0 | 0.018856 | 0.34286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015845 | 0 | 0 | 0 | 0 | 0.018856 | 0.34286 | 67 | 0.0026408 | 0 | 0 | 0 | 0 | 0.0031427 | 0.028571 |  | E | 13 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.015845 | 0 | 0 | 0.1 | 0 | 0.037712 | 0.34286 | 67 | 0.0026408 | 0 | 0 | 0.0083333 | 0 | 0.0062854 | 0.028571
Mechanical ventilation | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 | 0 |  | 0 | 4 | 100% |  | 0% |  | None | On site storage of electricity (e.g. electric battery) | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | 1 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | None | Scheduling electricity consumption (plug loads, white goods, etc.) | Automated management of local electricity consumption based on current renewable energy availability | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | E | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 40 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0.065712 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0 | 0.021904 | 0 | 0.016667 | 0 | 0 | 0
| E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | CHP control based on scheduled runtime management and/or current heat energy demand | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | 0 | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 2 | 2 | E | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 53 | 2 | 2 | 0 | 1 | 0 | 0 | 0 | 0.031689 | 0.043808 | 0 | 0.1 | 0 | 0 | 0 | 67 | 0.0052815 | 0.014603 | 0 | 0.0083333 | 0 | 0 | 0
| E-8 | DSM- Storage | Support of (micro)grid operation modes | 1 | 1 | 0 |  | 1 | 0 | 100% |  | 0% |  | None | Automated management of (building-level) electricity consumption based on grid signals | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | E | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 68 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0.065712 | 0 | 0.3 | 0 | 0 | 0 | 67 | 0 | 0.021904 | 0 | 0.025 | 0 | 0 | 0
| E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 | 0 |  | 1 | 2 | 100% |  | 0% |  | None | Current state of charge (SOC) data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | E | 82 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0.015845 | 0 | 0 | 0 | 0 | 0.018856 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015845 | 0 | 0 | 0 | 0 | 0.018856 | 0.22857 | 67 | 0.0026408 | 0 | 0 | 0 | 0 | 0.0031427 | 0.019048 |  | E | 84 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.015845 | 0 | 0 | 0.1 | 0 | 0.037712 | 0.34286 | 67 | 0.0026408 | 0 | 0 | 0.0083333 | 0 | 0.0062854 | 0.028571
| E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 | 1 |  | 1 | 2 | 100% |  | 0% |  | None | reporting on current electricity consumption on building level | real-time feedback or benchmarking on building level | real-time feedback or benchmarking on appliance level | real-time feedback or benchmarking on appliance level with automated personalized recommendations | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | E | 96 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0.015845 | 0 | 0 | 0 | 0 | 0 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015845 | 0 | 0 | 0 | 0 | 0 | 0.22857 | 67 | 0.0026408 | 0 | 0 | 0 | 0 | 0 | 0.019048 |  | E | 98 | 3 | 0 | 0 | 1 | 0 | 2 | 3 | 0.047534 | 0 | 0 | 0.1 | 0 | 0.037712 | 0.34286 | 67 | 0.0079223 | 0 | 0 | 0.0083333 | 0 | 0.0062854 | 0.028571
| EV-15 | EV Charging | EV Charging Capacity | 1 | 0 | 0 |  | 1 | 2 | 100% |  | 0% |  | not present | ducting (or simple power plug) available | 0-9% of parking spaces has recharging points | 10-50% or parking spaces has recharging point | >50% of parking spaces has recharging point | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 0 | 0 |  | 1 | 0 | 100% |  | 0% |  | Not present (uncontrolled charging) | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 2 | 0 | EV | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 0 | 0 |  | 1 | 1 | 100% |  | 0% |  | No information available | Reporting information on EV charging status to occupant | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 2 | 0 | EV | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | MC-3 | HVAC interaction control | Run time management of HVAC systems | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | Manual setting | Runtime setting of heating and cooling plants following a predefined time schedule | Heating and cooling plant on/off control based on building loads | Heating and cooling plant on/off control based on predictive control or grid signals | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | MC | 10 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 67 | 0.033333 | 0.066667 | 0.016667 | 0.016667 | 0 | 0 | 0 |  | MC | 12 | 3 | 2 | 2 | 3 | 1 | 0 | 0 | 0.6 | 0.4 | 0.4 | 0.6 | 0.2 | 0 | 0 | 67 | 0.1 | 0.13333 | 0.033333 | 0.05 | 0.016667 | 0 | 0
| MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | No central indication of detected faults and alarms | With central indication of detected faults and alarms for at least 2 relevant TBS | With central indication of detected faults and alarms for all relevant TBS | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | MC | 24 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 67 | 0 | 0 | 0 | 0.016667 | 0.016667 | 0.033333 | 0.016667 |  | MC | 26 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 67 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.05
Dynamic building envelope | MC-9 | TBS interaction control | Occupancy detection: connected services | 1 | 1 | 1 |  | 1 | 0 | 100% |  | 0% |  | None | Occupancy detection for individual functions, e.g. lighting | Centralised occupant detection which feeds in to several TBS such as lighting and heating | 0 | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 2 | 2 | MC | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 40 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 0.2 | 0 | 0.2 | 0.2 | 0 | 0.4 | 0 | 67 | 0.033333 | 0 | 0.016667 | 0.016667 | 0 | 0.066667 | 0
| MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 | 1 |  | 1 | 0 | 100% |  | 0% |  | None | Central or remote reporting of realtime energy use per energy carrier | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | 0 | 1 | 1 |  |  | 1 | 0 | 0 | 3 | 3 | MC | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 57 | 1 | 0 | 0 | 3 | 0 | 3 | 3 | 0.2 | 0 | 0 | 0.6 | 0 | 0.6 | 0.6 | 67 | 0.033333 | 0 | 0 | 0.05 | 0 | 0.1 | 0.05
| MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | None - No harmonization between grid and TBS; building is operated independently from the grid load | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Coordinated demand side management of multiple TBS | 0 | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 2 | 2 | MC | 71 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0.13333 | 0 | 0 | 0 | 0 | 0 |  | MC | 72 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.6 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0.033333 | 0.2 | 0 | 0.016667 | 0 | 0 | 0
| MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | None | Reporting information on current DSM status, including managed energy flows | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | 0 | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 2 | 2 | MC | 86 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.4 | 67 | 0 | 0.066667 | 0 | 0 | 0 | 0 | 0.033333 |  | MC | 87 | 0 | 2 | 0 | 0 | 0 | 1 | 3 | 0 | 0.4 | 0 | 0 | 0 | 0.2 | 0.6 | 67 | 0 | 0.13333 | 0 | 0 | 0 | 0.033333 | 0.05
Energy generation | MC-29 | Override control | Override of DSM control | 1 | 1 | 1 |  | 1 | 2 | 100% |  | 0% |  | No DSM control | DSM control without the possibility to override this control by the building user (occupant or facility manager) | Manual override and reactivation of DSM control by the building user | Scheduled override of DSM control (and reactivation) by the building user | Scheduled override of DSM control and reactivation with optimised control | 1 | 1 |  |  | 1 | 2 | 0 | 4 | 4 | MC | 101 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0 | 0.066667 | 0 | 0.016667 | 0 | 0 | 0 |  | MC | 103 | 0 | 2 | 0 | 3 | 0 | 1 | 0 | 0 | 0.4 | 0 | 0.6 | 0 | 0.2 | 0 | 67 | 0 | 0.13333 | 0 | 0.05 | 0 | 0.033333 | 0
| MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 | 1 |  | 1 | 1 | 100% |  | 0% |  | None | Single platform that allows manual control of multiple TBS | Single platform that allows automated control & coordination between TBS | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 0 | 1 | 1 |  |  | 1 | 1 | 0 | 3 | 3 | MC | 114 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 67 | 0 | 0 | 0 | 0.016667 | 0 | 0.033333 | 0 |  | MC | 116 | 2 | 0 | 0 | 3 | 0 | 1 | 0 | 0.4 | 0 | 0 | 0.6 | 0 | 0.2 | 0 | 67 | 0.066667 | 0 | 0 | 0.05 | 0 | 0.033333 | 0
| H-E1 | User defined service group 1 | User defined smart ready service 1 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | H | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| H-E2 | User defined service group 2 | User defined smart ready service 2 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | H | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| H-E3 | User defined service group 3 | User defined smart ready service 3 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | H | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| H-E4 | User defined service group 4 | User defined smart ready service 4 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | H | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| H-E5 | User defined service group 5 | User defined smart ready service 5 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | H | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 30.2% | 41.75% | 16% | 10% | 16% | 35.94% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | H | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-E1 | User defined service group 6 | User defined smart ready service 6 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-E2 | User defined service group 7 | User defined smart ready service 7 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-E3 | User defined service group 8 | User defined smart ready service 8 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-E4 | User defined service group 9 | User defined smart ready service 9 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-E5 | User defined service group 10 | User defined smart ready service 10 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DHW | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 10.73% | 14.83% | 0% | 10% | 0% | 12.77% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DHW | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C-E1 | User defined service group 11 | User defined smart ready service 11 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | C | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C-E2 | User defined service group 12 | User defined smart ready service 12 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | C | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C-E3 | User defined service group 13 | User defined smart ready service 13 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | C | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C-E4 | User defined service group 14 | User defined smart ready service 14 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | C | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C-E5 | User defined service group 15 | User defined smart ready service 15 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | C | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 11.74% | 16.23% | 16% | 10% | 16% | 13.98% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V-E1 | User defined service group 16 | User defined smart ready service 16 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | V | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V-E2 | User defined service group 17 | User defined smart ready service 17 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | V | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V-E3 | User defined service group 18 | User defined smart ready service 18 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | V | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V-E4 | User defined service group 19 | User defined smart ready service 19 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | V | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V-E5 | User defined service group 20 | User defined smart ready service 20 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | V | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 8.769% | 0% | 16% | 10% | 16% | 10.44% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | V | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L-E1 | User defined service group 21 | User defined smart ready service 21 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | L | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L-E2 | User defined service group 22 | User defined smart ready service 22 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | L | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L-E3 | User defined service group 23 | User defined smart ready service 23 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | L | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L-E4 | User defined service group 24 | User defined smart ready service 24 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | L | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L-E5 | User defined service group 25 | User defined smart ready service 25 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | L | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 11.98% | 0% | 16% | 10% | 16% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | L | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DE-E1 | User defined service group 26 | User defined smart ready service 26 | 0 | 0 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DE-E2 | User defined service group 27 | User defined smart ready service 27 | 0 | 0 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DE-E3 | User defined service group 28 | User defined smart ready service 28 | 0 | 0 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DE-E4 | User defined service group 29 | User defined smart ready service 29 | 0 | 0 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DE-E5 | User defined service group 30 | User defined smart ready service 30 | 0 | 0 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | DE | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 0% | 16% | 10% | 16% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E-E1 | User defined service group 31 | User defined smart ready service 31 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E-E2 | User defined service group 32 | User defined smart ready service 32 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E-E3 | User defined service group 33 | User defined smart ready service 33 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E-E4 | User defined service group 34 | User defined smart ready service 34 | 0 | 1 | 0 |  | 1 |  | 100% |  | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E-E5 | User defined service group 35 | User defined smart ready service 35 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | E | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.584% | 2.19% | 0% | 10% | 0% | 1.886% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | E | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-E1 | User defined service group 36 | User defined smart ready service 36 | 0 | 0 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-E2 | User defined service group 37 | User defined smart ready service 37 | 0 | 0 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-E3 | User defined service group 38 | User defined smart ready service 38 | 0 | 0 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-E4 | User defined service group 39 | User defined smart ready service 39 | 0 | 0 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EV-E5 | User defined service group 40 | User defined smart ready service 40 | 0 | 0 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | EV | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MC-E1 | User defined service group 41 | User defined smart ready service 41 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | MC | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MC-E2 | User defined service group 42 | User defined smart ready service 42 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | MC | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MC-E3 | User defined service group 43 | User defined smart ready service 43 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | MC | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MC-E4 | User defined service group 44 | User defined smart ready service 44 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | MC | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MC-E5 | User defined service group 45 | User defined smart ready service 45 | 0 | 1 | 0 |  | 1 |  | 100% | 0 | 0% |  | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  |  | 0 | 0 | 0 | 4 | 0 | MC | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on Z3: Ma Yixiao: The service should be included in the max score if: 1. If domain is present AND service is always to be assessed 2. If domain is present AND service is under triage but indicated as applicable by assessor 3. If domain is not present but mandatory; 4. If the service is switched on by the MS at high level

## Results
Smart Readiness Indicator for Buildings
The SRI calculations have been performed with an experimental tool. Please note that the scores and the visual presentation of results are solely provided for testing purposes. Using this experimental tool can by no means lead to any claims on an actual score or certificate for a building.
SRI spreadsheet tool Version 4.5
TOTAL SRI SCORE |  | 32.78% |  |  | SRI CLASS | Between 20% and 35%
IMPACT SCORES
Energy efficiency |  | 42.66%
Energy flexibility and storage |  | 21.61%
Comfort |  | 49.66%
Convenience |  | 25.97%
Health, well-being and accessibility |  | 44.57%
Maintenance and fault prediction |  | 24.49%
Information to occupants |  | 52.38%
BEWARE range for domains to be updated manually if services are added or removed!
DOMAIN SCORES | [9 empty] | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
[10 empty] | 16.67% | 33.33% | 8.333% | 8.333% | 8.333% | 16.67% | 8.333%
Heating |  | 39.99% | [6 empty] | Heating | 63.16% | 18.18% | 60% | 37.5% | 66.67% | 25% | 66.67% | 39.99%
Domestic hot water |  | 20.67% | [6 empty] | Domestic hot water | 20% | 0% | #DIV/0! | 0% | #DIV/0! | 50% | 66.67% | 20.67%
Cooling |  | 32.47% | [6 empty] | Cooling | 35% | 9.091% | 50% | 50% | 66.67% | 25% | 66.67% | 32.47%
Ventilation |  | 49.1% | [6 empty] | Ventilation | 35.71% | #DIV/0! | 70% | 62.5% | 55.56% | 50% | 33.33% | 49.1%
Lighting |  | 0% | [6 empty] | Lighting | 0% | #DIV/0! | 0% | 0% | 0% | #DIV/0! | #DIV/0! | 0%
Dynamic building envelope |  | 0% | [6 empty] | Dynamic building envelope | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
Electricity |  | 23.02% | [6 empty] | Electricity | 42.86% | 0% | #DIV/0! | 0% | #DIV/0! | 33.33% | 77.78% | 23.02%
Electric vehicle charging |  | 0% | [6 empty] | Electric vehicle charging | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
Monitoring and control |  | 33.23% | [6 empty] | Monitoring and control | 12.5% | 55.56% | 33.33% | 23.53% | 25% | 18.18% | 33.33% | 33.23%
DETAILED SCORES | [7 empty] | valid? | Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  | Domestic hot water | 1 | 1 | 0 | 1 | 0 | 1 | 1
Heating | 63.16% | 18.18% | 60% | 37.5% | 66.67% | 25% | 66.67% |  | Cooling | 1 | 1 | 1 | 1 | 1 | 1 | 1
Domestic hot water | 20% | 0% | 0% | 0% | 0% | 50% | 66.67% |  | Ventilation | 1 | 0 | 1 | 1 | 1 | 1 | 1
Cooling | 35% | 9.091% | 50% | 50% | 66.67% | 25% | 66.67% |  | Lighting | 1 | 0 | 1 | 1 | 1 | 0 | 0
Ventilation | 35.71% | 0% | 70% | 62.5% | 55.56% | 50% | 33.33% |  | Dynamic building envelope | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Electricity | 1 | 1 | 0 | 1 | 0 | 1 | 1
Dynamic building envelope | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Electric vehicle charging | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electricity | 42.86% | 0% | 0% | 0% | 0% | 33.33% | 77.78% |  | Monitoring and control | 1 | 1 | 1 | 1 | 1 | 1 | 1
Electric vehicle charging | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Monitoring and control | 12.5% | 55.56% | 33.33% | 23.53% | 25% | 18.18% | 33.33%
[8 empty] | score if valid | Heating | 63.16% | 18.18% | 60% | 37.5% | 66.67% | 25% | 66.67%
[9 empty] | Domestic hot water | 20% | 0% | 0% | 0% | 0% | 50% | 66.67%
[9 empty] | Cooling | 35% | 9.091% | 50% | 50% | 66.67% | 25% | 66.67%
AGGREGATED SCORES | [8 empty] | Ventilation | 35.71% | 0% | 70% | 62.5% | 55.56% | 50% | 33.33%
Key functionality 1 - building | 33.57% | [7 empty] | Lighting | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Key functionality 2 - user | 43.15% | [7 empty] | Dynamic building envelope | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Key functionality 3 - grid | 21.61% | [7 empty] | Electricity | 42.86% | 0% | 0% | 0% | 0% | 33.33% | 77.78%
[9 empty] | Electric vehicle charging | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[9 empty] | Monitoring and control | 12.5% | 55.56% | 33.33% | 23.53% | 25% | 18.18% | 33.33%
[9 empty] | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[8 empty] | weighting if valid | Heating | 16.67% | 33.33% | 8.333% | 8.333% | 8.333% | 16.67% | 8.333%
[9 empty] | Domestic hot water | 16.67% | 33.33% | 0% | 8.333% | 0% | 16.67% | 8.333%
[9 empty] | Cooling | 16.67% | 33.33% | 8.333% | 8.333% | 8.333% | 16.67% | 8.333%
[9 empty] | Ventilation | 16.67% | 0% | 8.333% | 8.333% | 8.333% | 16.67% | 8.333%
[9 empty] | Lighting | 16.67% | 0% | 8.333% | 8.333% | 8.333% | 0% | 0%
[9 empty] | Dynamic building envelope | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[9 empty] | Electricity | 16.67% | 33.33% | 0% | 8.333% | 0% | 16.67% | 8.333%
[9 empty] | Electric vehicle charging | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[9 empty] | Monitoring and control | 16.67% | 33.33% | 8.333% | 8.333% | 8.333% | 16.67% | 8.333%
Note on W23: Aerts Dorien: In the values below a check is added to avoid NaNs (div/0)

## Weightings
USER DEFINED
User-defined
DOMAIN WEIGHTINGS
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
Heating | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Domestic hot water | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Cooling | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Ventilation | 11.11% | 12.5% | 16.67% | 11.11% | 40% | 14.29% | 12.5%
Lighting | 11.11% | 0% | 16.67% | 11.11% | 0% | 0% | 0%
Electricity | 11.11% | 12.5% | 0% | 11.11% | 0% | 14.29% | 12.5%
Dynamic building envelope | 11.11% | 12.5% | 16.67% | 11.11% | 60% | 14.29% | 12.5%
Electric vehicle charging | 11.11% | 12.5% | 0% | 11.11% | 0% | 0% | 12.5%
Monitoring and control | 11.11% | 12.5% | 0% | 11.11% | 0% | 14.29% | 12.5%
| 100% | 100% | 100% | 100% | 100% | 100% | 100%
IMPACT WEIGHTINGS
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 100%
NOTE: some cells are set to zero and cannot be changed. This means that for these domains, the services have no impact on the given impact criterion.
=> no weight should be attributed.
DEFAULT WEIGHTING FACTORS
residential
DOMAIN WEIGHTINGS
North Europe | [9 empty] | West Europe | [8 empty] | South Europe | [8 empty] | North-East Europe | [8 empty] | South-East Europe | [9 empty] | A | B | A | B
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Comfort | Comfort | Health & Wellbeing | Health & Wellbeing
Heating | 0.29909 | 0.42673 | 0.16 | 0.1 | 0.16 | 0.3146 | 0.11429 |  |  | Heating | 0.33967 | 0.45722 | 0.16 | 0.1 | 0.16 | 0.34643 | 0.11429 |  | Heating | 0.31666 | 0.37624 | 0.16 | 0.1 | 0.16 | 0.3284 | 0.11429 |  | Heating | 0.30383 | 0.41172 | 0.16 | 0.1 | 0.16 | 0.30636 | 0.11429 |  | Heating | 0.20621 | 0.24438 | 0.16 | 0.1 | 0.16 | 0.20871 | 0.11429 |  | Heating | 0.2 | 0.16 | 0.25 | 0.16
Domestic hot water | 0.092805 | 0.13241 | 0 | 0.1 | 0 | 0.097617 | 0.11429 |  |  | Domestic hot water | 0.07621 | 0.10258 | 0 | 0.1 | 0 | 0.077729 | 0.11429 |  | Domestic hot water | 0.099794 | 0.11857 | 0 | 0.1 | 0 | 0.10349 | 0.11429 |  | Domestic hot water | 0.13928 | 0.18873 | 0 | 0.1 | 0 | 0.14044 | 0.11429 |  | Domestic hot water | 0.058032 | 0.068776 | 0 | 0.1 | 0 | 0.058737 | 0.11429 |  | Domestic hot water | 0 | 0 | 0 | 0
Cooling | 0 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0.11429 |  |  | Cooling | 0.030389 | 0.040906 | 0.16 | 0.1 | 0.16 | 0.030995 | 0.11429 |  | Cooling | 0.068809 | 0.081755 | 0.16 | 0.1 | 0.16 | 0.07136 | 0.11429 |  | Cooling | 0 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0.11429 |  | Cooling | 0.14659 | 0.17373 | 0.16 | 0.1 | 0.16 | 0.14837 | 0.11429 |  | Cooling | 0.2 | 0.16 | 0.25 | 0.16
Ventilation | 0.18736 | 0 | 0.16 | 0.1 | 0.16 | 0.19708 | 0.11429 |  |  | Ventilation | 0.17817 | 0 | 0.16 | 0.1 | 0.16 | 0.18172 | 0.11429 |  | Ventilation | 0.091952 | 0 | 0.16 | 0.1 | 0.16 | 0.095361 | 0.11429 |  | Ventilation | 0.19033 | 0 | 0.16 | 0.1 | 0.16 | 0.19192 | 0.11429 |  | Ventilation | 0.10816 | 0 | 0.16 | 0.1 | 0.16 | 0.10948 | 0.11429 |  | Ventilation | 0.2 | 0.16 | 0.25 | 0.16
Lighting | 0.036968 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  |  | Lighting | 0.014649 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.026813 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.0062019 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.0089994 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.2 | 0.16 | 0 | 0.16
Electricity | 0.13377 | 0.19086 | 0 | 0.1 | 0 | 0.14071 | 0.11429 |  |  | Electricity | 0.11091 | 0.14929 | 0 | 0.1 | 0 | 0.11312 | 0.11429 |  | Electricity | 0.14597 | 0.17343 | 0 | 0.1 | 0 | 0.15138 | 0.11429 |  | Electricity | 0.11036 | 0.14955 | 0 | 0.1 | 0 | 0.11128 | 0.11429 |  | Electricity | 0.22201 | 0.26311 | 0 | 0.1 | 0 | 0.2247 | 0.11429 |  | Electricity | 0 | 0 | 0 | 0
Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.2 | 0.16 | 0.25 | 0.16
Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0 | 0 | 0
Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0 | 0.2 | 0 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [9 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
non-residential
DOMAIN WEIGHTINGS
North Europe | [9 empty] | West Europe | [8 empty] | South Europe | [8 empty] | North-East Europe | [8 empty] | South-East Europe
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
Heating | 0.31322 | 0.49384 | 0.16 | 0.1 | 0.16 | 0.34962 | 0.11429 |  |  | Heating | 0.27278 | 0.40662 | 0.16 | 0.1 | 0.16 | 0.31659 | 0.11429 |  | Heating | 0.30198 | 0.41746 | 0.16 | 0.1 | 0.16 | 0.35938 | 0.11429 |  | Heating | 0.29248 | 0.44428 | 0.16 | 0.1 | 0.16 | 0.32403 | 0.11429 |  | Heating | 0.28706 | 0.42184 | 0.16 | 0.1 | 0.16 | 0.32574 | 0.11429
Domestic hot water | 0.053686 | 0.084645 | 0 | 0.1 | 0 | 0.059926 | 0.11429 |  |  | Domestic hot water | 0.082585 | 0.12311 | 0 | 0.1 | 0 | 0.095848 | 0.11429 |  | Domestic hot water | 0.10727 | 0.1483 | 0 | 0.1 | 0 | 0.12766 | 0.11429 |  | Domestic hot water | 0.093878 | 0.1426 | 0 | 0.1 | 0 | 0.10401 | 0.11429 |  | Domestic hot water | 0.11572 | 0.17006 | 0 | 0.1 | 0 | 0.13131 | 0.11429
Cooling | 0.093696 | 0.14773 | 0.16 | 0.1 | 0.16 | 0.10459 | 0.11429 |  |  | Cooling | 0.1267 | 0.18887 | 0.16 | 0.1 | 0.16 | 0.14705 | 0.11429 |  | Cooling | 0.11743 | 0.16234 | 0.16 | 0.1 | 0.16 | 0.13975 | 0.11429 |  | Cooling | 0.083878 | 0.12741 | 0.16 | 0.1 | 0.16 | 0.092927 | 0.11429 |  | Cooling | 0.074586 | 0.1096 | 0.16 | 0.1 | 0.16 | 0.084635 | 0.11429
Ventilation | 0.19621 | 0 | 0.16 | 0.1 | 0.16 | 0.21902 | 0.11429 |  |  | Ventilation | 0.14309 | 0 | 0.16 | 0.1 | 0.16 | 0.16607 | 0.11429 |  | Ventilation | 0.087687 | 0 | 0.16 | 0.1 | 0.16 | 0.10435 | 0.11429 |  | Ventilation | 0.18322 | 0 | 0.16 | 0.1 | 0.16 | 0.20299 | 0.11429 |  | Ventilation | 0.15058 | 0 | 0.16 | 0.1 | 0.16 | 0.17087 | 0.11429
Lighting | 0.078094 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  |  | Lighting | 0.10378 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.11979 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.073036 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0 |  | Lighting | 0.089049 | 0 | 0.16 | 0.1 | 0.16 | 0 | 0
Electricity | 0.01509 | 0.023792 | 0 | 0.1 | 0 | 0.016844 | 0.11429 |  |  | Electricity | 0.021067 | 0.031404 | 0 | 0.1 | 0 | 0.02445 | 0.11429 |  | Electricity | 0.015845 | 0.021904 | 0 | 0.1 | 0 | 0.018856 | 0.11429 |  | Electricity | 0.023509 | 0.03571 | 0 | 0.1 | 0 | 0.026045 | 0.11429 |  | Electricity | 0.033001 | 0.048496 | 0 | 0.1 | 0 | 0.037447 | 0.11429
Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429 |  | Dynamic building envelope | 0.05 | 0 | 0.16 | 0.1 | 0.16 | 0.05 | 0.11429
Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric vehicle charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring and control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [9 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants |  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
RELEVANCE OF DOMAIN TO IMPACT CRITERION (for verification of domain weightings)
LEGEND
0 | the services within this domain have no contribution to the given impact criterion
1 | at least one service within this domain contributes to the given impact criterion
Method A | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | Method B | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1
Domestic hot water | 1 | 1 | 0 | 1 | 0 | 1 | 1 | Domestic hot water | 1 | 1 | 0 | 1 | 0 | 1 | 1
Cooling | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Cooling | 1 | 1 | 1 | 1 | 1 | 1 | 1
Ventilation | 1 | 0 | 1 | 1 | 1 | 1 | 1 | Ventilation | 1 | 0 | 1 | 1 | 1 | 1 | 1
Lighting | 1 | 0 | 1 | 1 | 0 | 0 | 0 | Lighting | 1 | 0 | 1 | 1 | 1 | 0 | 0
Electricity | 1 | 1 | 0 | 1 | 0 | 1 | 1 | Electricity | 1 | 1 | 0 | 1 | 0 | 1 | 1
Dynamic building envelope | 1 | 0 | 1 | 1 | 1 | 1 | 1 | Dynamic building envelope | 1 | 0 | 1 | 1 | 1 | 1 | 1
Electric vehicle charging | 0 | 1 | 0 | 1 | 0 | 0 | 1 | Electric vehicle charging | 0 | 1 | 0 | 1 | 0 | 0 | 1
Monitoring and control | 1 | 1 | 0 | 1 | 0 | 1 | 1 | Monitoring and control | 1 | 1 | 1 | 1 | 1 | 1 | 1
ENERGY BALANCE DATA
RESIDENTIAL | WEIGHTINGS | North | West | South | North-East | South-East
| Heating | 39.8787 | 45.2891 | 42.2219 | 40.5106 | 27.4941
| DHW | 12.374 | 10.1614 | 13.3059 | 18.5702 | 7.7376
| Cooling | 0 | 4.0519 | 9.1745 | 0 | 19.5457
| Ventilation | 24.9819 | 23.7563 | 12.2602 | 25.3777 | 14.4219
| Lighting | 4.929 | 1.9532 | 3.575 | 0.82692 | 1.1999
| Electricity | 17.8363 | 14.7881 | 19.4624 | 14.7145 | 29.6008
|  | 3 | 4 | 5 | 6 | 7
NON RESIDENTIAL | WEIGHTINGS | North | West | South | North-East | South-East
| Heating | 41.7625 | 36.3708 | 40.2637 | 38.9971 | 38.2751
| DHW | 7.1582 | 11.0113 | 14.3029 | 12.5171 | 15.4297
| Cooling | 12.4928 | 16.8935 | 15.6576 | 11.1837 | 9.9448
| Ventilation | 26.162 | 19.0782 | 11.6916 | 24.4296 | 20.0771
| Lighting | 10.4125 | 13.8372 | 15.9716 | 9.7381 | 11.8732
| Electricity | 2.012 | 2.8089 | 2.1126 | 3.1345 | 4.4002
Note on A14: Christina Protopapadaki: Notice: Different order of domains here: Electricity and Dynamic building envelope inversed compaired to other tabs.

## overview_of_services
Domain | Code | Service group | Smart ready service | Functionality level 0 (as non-smart default) | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4 | part of the method A: 1 - YES; 0 - NO | part of the method B: 1 - YES; 0 - NO | part of the custom services list?: 1 - YES; 0 - NO | Preconditions / Dependency on other services or building types | TRIAGE: 1 - This service affects maximum obtainable score, even if service is not applicable in this building; 0 - This service does not affect maximum obtainable score when not present in building | 15 | Service included in the selected method (A/B/custom): 0 - not included, 1 - included | 1 - This domain is present; 2 - This domain is absent but mandatory; 0 - This domain is absent and not mandatory
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | part of the method B: 1 - YES; 0 - NO |  |  | 0 |  | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | part of the custom services list?: 1 - YES; 0 - NO |  |  | 0 |  | 0
Heating | H-1a | Heat control - demand side | Heat emission control | No automatic control | Central automatic control (e.g. central thermostat) | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | H | 1 | 1
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | H | 1 | 1
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | No automatic control | Outside temperature compensated control | Demand based control |  |  | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | H | 1 | 1
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | H | 1 | 1
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Heat storage capable of flexible control through grid signals (e.g. DSM) |  | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | H | 1 | 1
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) |  |  | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | H | 1 | 1
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | On/Off-control of heat generator | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of heat generator capacity depending on the load AND external signals from grid |  | 1 | 1 |  | Only applicable in case of heat pumps | 0 | H | 1 | 1
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | H | 1 | 1
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  | 0 | 1 | H | 1 | 1
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | No automatic control | Scheduled operation of heating system | Self-learning optimal control of heating system | Heating system capable of flexible control through grid signals (e.g. DSM) | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | H | 1 | 1
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) |  | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | DHW | 1 | 1
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) |  | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | DHW | 1 | 1
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | Manual selected control of solar energy or heat generation | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management |  | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | DHW | 1 | 1
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | DHW | 1 | 1
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  | 0 | 1 | DHW | 1 | 1
Cooling | C-1a | Cooling control - demand side | Cooling emission control | No automatic control | Central automatic control | Individual room control | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | C | 1 | 1
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | C | 1 | 1
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | Constant temperature control | Outside temperature compensated control | Demand based control |  |  | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | C | 1 | 1
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | C | 1 | 1
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | No interlock | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Total interlock (control system ensures no simultaneous heating and cooling can take place) |  |  | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | C | 1 | 1
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Cold storage capable of flexible control through grid signals (e.g. DSM) |  | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | C | 1 | 1
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | On/Off-control of cooling production | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of cooling production capacity depending on the load AND external signals from grid |  | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | C | 1 | 1
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | Priorities only based on running times | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Sequencing based on dynamic priority list, including external signals from grid | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | C | 1 | 1
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | C | 1 | 1
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | No automatic control | Scheduled operation of cooling system | Self-learning optimal control of cooling system | Cooling system capable of flexible control through grid signals (e.g. DSM) | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | C | 1 | 1
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | No ventilation system or manual control | Clock control | Occupancy detection control | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 1 | 1 |  | Always to be assessed | 1 | V | 1 | 1
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | Multi-stage control: To reduce the auxiliary energy demand of the fan | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | 0 | 1 |  | Only in case of mechanical ventilation | 0 | V | 1 | 1
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | Without overheating control | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control |  |  | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | V | 1 | 1
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | No automatic control | Constant setpoint: A control loop enables to control the supply air_x000D_ temperature, the setpoint is constant and can only be modified by a manual_x000D_ action | Variable set point with outdoor temperature compensation | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room |  | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | V | 1 | 1
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | No automatic control | Night cooling | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical_x000D_ cooling | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). |  | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | V | 1 | 1
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | None | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) |  | 1 | 1 |  | Always to be assessed | 1 | V | 1 | 1
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | Manual on/off switch | Manual on/off switch + additional sweeping extinction signal | Automatic detection (auto on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) |  | 1 | 1 |  | Always to be assessed | 1 | L | 1 | 1
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | Manual (central) | Manual (per room / zone) | Automatic switching | Automatic dimming | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | 0 | 1 |  | Always to be assessed | 1 | L | 1 | 1
Dynamic building envelope | DE-1 | Window control | Window solar shading control | No sun shading or only manual operation | Motorized operation with manual control | Motorized operation with automatic control based on sensor data | Combined light/blind/HVAC control | Predictive blind control (e.g. based on weather forecast) | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | DE | 1 | 0
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | Manual operation or only fixed windows | Open/closed detection to shut down heating or cooling systems | Level 1 + Automised mechanical window opening based on room sensor data | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling |  | 0 | 1 |  | 0 | 1 | DE | 1 | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | No reporting | Position of each product & fault detection | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | DE | 1 | 0
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | None | Current generation data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  | Only applicable in case of local energy generation | 0 | E | 1 | 1
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | None | On site storage of electricity (e.g. electric battery) | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | 1 | 1 |  | Only applicable in case of local energy generation | 0 | E | 1 | 1
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | None | Scheduling electricity consumption (plug loads, white goods, etc.) | Automated management of local electricity consumption based on current renewable energy availability | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability |  | 0 | 1 |  | Only applicable in case of local energy generation | 0 | E | 1 | 1
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | CHP control based on scheduled runtime management and/or current heat energy demand | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables |  |  | 0 | 1 |  | Only applicable in case of CHP | 0 | E | 1 | 1
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | None | Automated management of (building-level) electricity consumption based on grid signals | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) |  | 0 | 1 |  | Only applicable in case of local energy storage | 0 | E | 1 | 1
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | None | Current state of charge (SOC) data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 1 |  | Only applicable in case of local energy storage | 0 | E | 1 | 1
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | None | reporting on current electricity consumption on building level | real-time feedback or benchmarking on building level | real-time feedback or benchmarking on appliance level | real-time feedback or benchmarking on appliance level with automated personalized recommendations | 1 | 1 |  | Always to be assessed | 1 | E | 1 | 1
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | not present | ducting (or simple power plug) available | 0-9% of parking spaces has recharging points | 10-50% or parking spaces has recharging point | >50% of parking spaces has recharging point | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | EV | 1 | 0
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | Not present (uncontrolled charging) | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) |  |  | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | EV | 1 | 0
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | No information available | Reporting information on EV charging status to occupant | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) |  |  | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | EV | 1 | 0
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | Manual setting | Runtime setting of heating and cooling plants following a predefined time schedule | Heating and cooling plant on/off control based on building loads | Heating and cooling plant on/off control based on predictive control or grid signals |  | 0 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | No central indication of detected faults and alarms | With central indication of detected faults and alarms for at least 2 relevant TBS | With central indication of detected faults and alarms for all relevant TBS | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions |  | 0 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | None | Occupancy detection for individual functions, e.g. lighting | Centralised occupant detection which feeds in to several TBS such as lighting and heating |  |  | 0 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | None | Central or remote reporting of realtime energy use per energy carrier | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface |  | 1 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | None - No harmonization between grid and TBS; building is operated independently from the grid load | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Coordinated demand side management of multiple TBS |  |  | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | MC | 1 | 1
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | None | Reporting information on current DSM status, including managed energy flows | Reporting information on currenthistorical and predicted DSM status, including managed energy flows |  |  | 0 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-29 | Override control | Override of DSM control | No DSM control | DSM control without the possibility to override this control by the building user (occupant or facility manager) | Manual override and reactivation of DSM control by the building user | Scheduled override of DSM control (and reactivation) by the building user | Scheduled override of DSM control and reactivation with optimised control | 0 | 1 |  | 0 | 1 | MC | 1 | 1
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | None | Single platform that allows manual control of multiple TBS | Single platform that allows automated control & coordination between TBS | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals |  | 1 | 1 |  | Always to be assessed | 1 | MC | 1 | 1
Heating | H-E1 | User defined service group 1 | User defined smart ready service 1 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | H
Heating | H-E2 | User defined service group 2 | User defined smart ready service 2 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | H
Heating | H-E3 | User defined service group 3 | User defined smart ready service 3 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | H
Heating | H-E4 | User defined service group 4 | User defined smart ready service 4 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | H
Heating | H-E5 | User defined service group 5 | User defined smart ready service 5 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | H
Domestic hot water | DHW-E1 | User defined service group 6 | User defined smart ready service 6 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DHW
Domestic hot water | DHW-E2 | User defined service group 7 | User defined smart ready service 7 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DHW
Domestic hot water | DHW-E3 | User defined service group 8 | User defined smart ready service 8 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DHW
Domestic hot water | DHW-E4 | User defined service group 9 | User defined smart ready service 9 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DHW
Domestic hot water | DHW-E5 | User defined service group 10 | User defined smart ready service 10 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DHW
Cooling | C-E1 | User defined service group 11 | User defined smart ready service 11 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | C
Cooling | C-E2 | User defined service group 12 | User defined smart ready service 12 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | C
Cooling | C-E3 | User defined service group 13 | User defined smart ready service 13 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | C
Cooling | C-E4 | User defined service group 14 | User defined smart ready service 14 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | C
Cooling | C-E5 | User defined service group 15 | User defined smart ready service 15 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | C
Ventilation | V-E1 | User defined service group 16 | User defined smart ready service 16 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | V
Ventilation | V-E2 | User defined service group 17 | User defined smart ready service 17 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | V
Ventilation | V-E3 | User defined service group 18 | User defined smart ready service 18 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | V
Ventilation | V-E4 | User defined service group 19 | User defined smart ready service 19 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | V
Ventilation | V-E5 | User defined service group 20 | User defined smart ready service 20 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | V
Lighting | L-E1 | User defined service group 21 | User defined smart ready service 21 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | L
Lighting | L-E2 | User defined service group 22 | User defined smart ready service 22 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | L
Lighting | L-E3 | User defined service group 23 | User defined smart ready service 23 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | L
Lighting | L-E4 | User defined service group 24 | User defined smart ready service 24 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | L
Lighting | L-E5 | User defined service group 25 | User defined smart ready service 25 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | L
Dynamic building envelope | DE-E1 | User defined service group 26 | User defined smart ready service 26 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DE
Dynamic building envelope | DE-E2 | User defined service group 27 | User defined smart ready service 27 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DE
Dynamic building envelope | DE-E3 | User defined service group 28 | User defined smart ready service 28 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DE
Dynamic building envelope | DE-E4 | User defined service group 29 | User defined smart ready service 29 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DE
Dynamic building envelope | DE-E5 | User defined service group 30 | User defined smart ready service 30 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | DE
Electricity | E-E1 | User defined service group 31 | User defined smart ready service 31 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | E
Electricity | E-E2 | User defined service group 32 | User defined smart ready service 32 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | E
Electricity | E-E3 | User defined service group 33 | User defined smart ready service 33 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | E
Electricity | E-E4 | User defined service group 34 | User defined smart ready service 34 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | E
Electricity | E-E5 | User defined service group 35 | User defined smart ready service 35 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | E
Electric vehicle charging | EV-E1 | User defined service group 36 | User defined smart ready service 36 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | EV
Electric vehicle charging | EV-E2 | User defined service group 37 | User defined smart ready service 37 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | EV
Electric vehicle charging | EV-E3 | User defined service group 38 | User defined smart ready service 38 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | EV
Electric vehicle charging | EV-E4 | User defined service group 39 | User defined smart ready service 39 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | EV
Electric vehicle charging | EV-E5 | User defined service group 40 | User defined smart ready service 40 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | EV
Monitoring and control | MC-E1 | User defined service group 41 | User defined smart ready service 41 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | MC
Monitoring and control | MC-E2 | User defined service group 42 | User defined smart ready service 42 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | MC
Monitoring and control | MC-E3 | User defined service group 43 | User defined smart ready service 43 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | MC
Monitoring and control | MC-E4 | User defined service group 44 | User defined smart ready service 44 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | MC
Monitoring and control | MC-E5 | User defined service group 45 | User defined smart ready service 45 | User defined level 1-0 | User defined level 1-1 | User defined level 1-2 | User defined level 1-3 | User defined level 1-4 | 0 | 0 |  | Please define your preconditions for this service | 0 | MC

## H
| Domain | Heating
| code | service | 1
► | H-1a | Heat emission control |  | Service group: | Heat control - demand side |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control (e.g. central thermostat) | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | H-1b | Emission control for TABS (heating mode) |  | Service group: | Heat control - demand side |  |  |  |  | line | 21
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | H-1c | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks |  | Service group: | Heat control - demand side |  |  |  |  | line | 35
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | A | [6 empty] | B
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | H-1d | Control of distribution pumps in networks |  | Service group: | Heat control - demand side |  |  |  |  | line | 49
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | H-1f | Thermal Energy Storage (TES) for building heating (excluding TABS) |  | Service group: | Heat control - demand side |  |  |  |  | line | 64
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Heat storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | H-2a | Heat generator control (all except heat pumps) |  | Service group: | Control heat production facilities |  |  |  |  | line | 80
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Variable temperature control depending on outdoor temperature | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | H-2b | Heat generator control (for heat pumps) |  | Service group: | Control heat production facilities |  |  |  |  | line | 94
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | On/Off-control of heat generator | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of heat generator capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
► | H-2d | Sequencing in case of different heat generators |  | Service group: | Control heat production facilities |  |  |  |  | line | 109
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | H-3 | Report information regarding heating system performance |  | Service group: | Information to occupants and facility managers |  |  |  |  | line | 125
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources
Standard?
| code | service | 0
| H-4 | Flexibility and grid interaction |  | Service group: | Flexibility and grid interaction |  |  |  |  | line | 139
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of heating system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of heating system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Heating system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0
Information sources
Standard?
| code | service | 0
| H-E1 | User defined smart ready service 1 |  | Service group: | User defined service group 1 |  |  |  |  | line | 153
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| H-E2 | User defined smart ready service 2 |  | Service group: | User defined service group 2 |  |  |  |  | line | 167
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| H-E3 | User defined smart ready service 3 |  | Service group: | User defined service group 3 |  |  |  |  | line | 181
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| H-E4 | User defined smart ready service 4 |  | Service group: | User defined service group 4 |  |  |  |  | line | 195
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| H-E5 | User defined smart ready service 5 |  | Service group: | User defined service group 5 |  |  |  |  | line | 209
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## DHW
| Domain | Domestic hot water
| code | service | 1
► | DHW-1a | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) |  | Service group: | Control DHW production facilities |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control on / off and scheduled charging enable and multi-sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | DHW-1b | Control of DHW storage charging (using hot water generation) |  | Service group: | Control DHW production facilities |  |  |  |  | line | 18
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants | A | [6 empty] | B
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | 2 | 3 | 0 | 2 | 0 | 0 | 0 | [7 empty] | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | DHW-1d | Control of DHW storage charging (with solar collector and supplymentary heat generation) |  | Service group: | Control DHW production facilities |  |  |  |  | line | 34
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual selected control of solar energy or heat generation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | 2 | 1 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | 3 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
| DHW-2b | Sequencing in case of different DHW generators |  | Service group: | Control DHW production facilities |  |  |  |  | line | 48
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 1
► | DHW-3 | Report information regarding domestic hot water performance |  | Service group: | Information to occupants and facility managers |  |  |  |  | line | 63
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service | 0
| DHW-E1 | User defined smart ready service 6 |  | Service group: | User defined service group 6 |  |  |  |  | line | 79
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DHW-E2 | User defined smart ready service 7 |  | Service group: | User defined service group 7 |  |  |  |  | line | 93
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DHW-E3 | User defined smart ready service 8 |  | Service group: | User defined service group 8 |  |  |  |  | line | 107
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DHW-E4 | User defined smart ready service 9 |  | Service group: | User defined service group 9 |  |  |  |  | line | 121
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DHW-E5 | User defined smart ready service 10 |  | Service group: | User defined service group 10 |  |  |  |  | line | 135
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## C
| Domain | Cooling
| code | service | 1
► | C-1a | Cooling emission control |  | Service group: | Cooling control - demand side |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-1b | Emission control for TABS (cooling mode) |  | Service group: | Cooling control - demand side |  |  |  |  | line | 18
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 1 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-1c | Control of distribution network chilled water temperature (supply or return) |  | Service group: | Cooling control - demand side |  |  |  |  | line | 32
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-1d | Control of distribution pumps in networks |  | Service group: | Cooling control - demand side |  |  |  |  | line | 46
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #VALUE! | + | 0 | + | + | 0 | 0 | 0
| level 2 | #VALUE! | ++ | 0 | + | + | 0 | 0 | 0
| level 3 | #VALUE! | +++ | 0 | + | + | 0 | 0 | 0
| level 4 | #VALUE!
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-1f | Interlock: avoiding simultaneous heating and cooling in the same room |  | Service group: | Cooling control - demand side |  |  |  |  | line | 72
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No interlock | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Total interlock (control system ensures no simultaneous heating and cooling can take place) | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-1g | Control of Thermal Energy Storage (TES) operation |  | Service group: | Cooling control - demand side |  |  |  |  | line | 86
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Cold storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | C-2a | Generator control for cooling |  | Service group: | Control cooling production facilities |  |  |  |  | line | 101
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | On/Off-control of cooling production | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of cooling production capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | C-2b | Sequencing of different cooling generators |  | Service group: | Control cooling production facilities |  |  |  |  | line | 115
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running times | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Sequencing based on dynamic priority list, including external signals from grid | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | C-3 | Report information regarding cooling system performance |  | Service group: | Information to occupants and facility managers |  |  |  |  | line | 129
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources
Standard?
| code | service | 1
| C-4 | Flexibility and grid interaction |  | Service group: | Flexibility and grid interaction |  |  |  |  | line | 143
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of cooling system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of cooling system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Cooling system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0
Information sources
Standard?
| code | service | 0
| C-E1 | User defined smart ready service 11 |  | Service group: | User defined service group 11 |  |  |  |  | line | 157
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| C-E2 | User defined smart ready service 12 |  | Service group: | User defined service group 12 |  |  |  |  | line | 171
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| C-E3 | User defined smart ready service 13 |  | Service group: | User defined service group 13 |  |  |  |  | line | 185
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| C-E4 | User defined smart ready service 14 |  | Service group: | User defined service group 14 |  |  |  |  | line | 199
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| C-E5 | User defined smart ready service 15 |  | Service group: | User defined service group 15 |  |  |  |  | line | 213
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## V
| Domain | Ventilation
| code | service | 1
► | V-1a | Supply air flow control at the room level |  | Service group: | Air flow control |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No ventilation system or manual control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Clock control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Occupancy detection control | 1 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | 2 | 0 | 3 | 3 | 3 | 0 | 0
| level 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | V-1c | Air flow or pressure control at the air handler level |  | Service group: | Air flow control |  |  |  |  | line | 20
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-stage control: To reduce the auxiliary energy demand of the fan | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | 3 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | V-2c | Heat recovery control: prevention of overheating |  | Service group: | Air temperature control |  |  |  |  | line | 37
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Without overheating control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Modulate or bypass heat recovery based on sensors in air exhaust | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | V-2d | Supply air temperature control at the air handling unit level |  | Service group: | Air temperature control |  |  |  |  | line | 51
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Constant setpoint: A control loop enables to control the supply air_x000D_ temperature, the setpoint is constant and can only be modified by a manual_x000D_ action | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Variable set point with outdoor temperature compensation | 2 | 0 | 2 | 1 | 0 | 0 | 0
| level 3 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | 3 | 0 | 2 | 1 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | V-3 | Free cooling with mechanical ventilation system |  | Service group: | Free cooling |  |  |  |  | line | 65
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Night cooling | 1 | 0 | 3 | 2 | 1 | 0 | 0
| level 2 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical_x000D_ cooling | 2 | 0 | 3 | 2 | 1 | 0 | 0
| level 3 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | 3 | 0 | 3 | 2 | 1 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #VALUE! | 0 | 0 | ++ | + | + | 0 | 0
| level 2 | #VALUE! | 0 | 0 | ++ | + | + | 0 | 0
| level 3 | #VALUE! | +++ | 0 | ++ | ++ | + | 0 | 0
| level 4 | #VALUE!
Information sources
Standard?
| code | service | 1
► | V-6 | Reporting information regarding IAQ |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 91
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | 0 | 0 | 0 | 0 | 2 | 1 | 1
| level 2 | Real time monitoring & historical information of IAQ available to occupants | 0 | 0 | 0 | 0 | 3 | 1 | 2
| level 3 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | 0 | 0 | 0 | 0 | 3 | 2 | 3
| level 4 | 0
Information sources
Standard?
| code | service | 0
| V-E1 | User defined smart ready service 16 |  | Service group: | User defined service group 16 |  |  |  |  | line | 106
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| V-E2 | User defined smart ready service 17 |  | Service group: | User defined service group 17 |  |  |  |  | line | 120
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| V-E3 | User defined smart ready service 18 |  | Service group: | User defined service group 18 |  |  |  |  | line | 134
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| V-E4 | User defined smart ready service 19 |  | Service group: | User defined service group 19 |  |  |  |  | line | 148
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| V-E5 | User defined smart ready service 20 |  | Service group: | User defined service group 20 |  |  |  |  | line | 162
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## L
| Domain | Lighting
| code | service | 1
► | L-1a | Occupancy control for indoor lighting |  | Service group: | Artificial lighting control |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual on/off switch | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual on/off switch + additional sweeping extinction signal | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic detection (auto on / dimmed or auto off) | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | Automatic detection (manual on / dimmed or auto off) | 3 | 0 | 2 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 0
► | L-2 | Control artificial lighting power based on daylight levels |  | Service group: | Control artificial lighting power based on daylight levels |  |  |  |  | line | 20
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual (central) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual (per room / zone) | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic switching | 2 | 0 | 1 | 1 | 1 | 0 | 0
| level 3 | Automatic dimming | 3 | 0 | 2 | 2 | 2 | 0 | 0
| level 4 | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15193-1 and CEN-TR 16791 | CEN-TR 16791 | EN 12464-1 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791
| code | service | 0
| L-E1 | User defined smart ready service 21 |  | Service group: | User defined service group 21 |  |  |  |  | line | 35
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| L-E2 | User defined smart ready service 22 |  | Service group: | User defined service group 22 |  |  |  |  | line | 49
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| L-E3 | User defined smart ready service 23 |  | Service group: | User defined service group 23 |  |  |  |  | line | 63
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| L-E4 | User defined smart ready service 24 |  | Service group: | User defined service group 24 |  |  |  |  | line | 77
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| L-E5 | User defined smart ready service 25 |  | Service group: | User defined service group 25 |  |  |  |  | line | 91
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## DE
| Domain | Dynamic building envelope
| code | service | 1
► | DE-1 | Window solar shading control |  | Service group: | Window control |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No sun shading or only manual operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Motorized operation with manual control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Motorized operation with automatic control based on sensor data | 2 | 0 | 1 | 2 | 1 | 0 | 0
| level 3 | Combined light/blind/HVAC control | 3 | 0 | 2 | 3 | 2 | 0 | 0
| level 4 | Predictive blind control (e.g. based on weather forecast) | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
Standard?
| code | service | 0
► | DE-2 | Window open/closed control, combined with HVAC system |  | Service group: | Window control |  |  |  |  | line | 18
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual operation or only fixed windows | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Open/closed detection to shut down heating or cooling systems | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Level 1 + Automised mechanical window opening based on room sensor data | 2 | 0 | 2 | 1 | 1 | 0 | 0
| level 3 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | 2 | 0 | 2 | 2 | 1 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
| DE-4 | Reporting information regarding performance of dynamic building envelope systems |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 34
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No reporting | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Position of each product & fault detection | 0 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Position of each product, fault detection & predictive maintenance | 0 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | 0 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | 0 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service | 0
| DE-E1 | User defined smart ready service 26 |  | Service group: | User defined service group 26 |  |  |  |  | line | 49
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DE-E2 | User defined smart ready service 27 |  | Service group: | User defined service group 27 |  |  |  |  | line | 63
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DE-E3 | User defined smart ready service 28 |  | Service group: | User defined service group 28 |  |  |  |  | line | 77
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DE-E4 | User defined smart ready service 29 |  | Service group: | User defined service group 29 |  |  |  |  | line | 91
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| DE-E5 | User defined smart ready service 30 |  | Service group: | User defined service group 30 |  |  |  |  | line | 105
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## E
| Domain | Electricity
| code | service | 1
► | E-2 | Reporting information regarding local electricity generation |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 5
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current generation data available | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
|  | Information sources | IEC 61850-7-420 | IEC 61850-7-420
Standard?
| code | service | 1
► | E-3 | Storage of (locally generated) electricity |  | Service group: | DER - Storage |  |  |  |  | line | 19
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On site storage of electricity (e.g. electric battery) | 0 | 1 | 0 | 2 | 0 | 0 | 0
| level 2 | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | 0 | 3 | 0 | 2 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
► | E-4 | Optimizing self-consumption of locally generated electricity |  | Service group: | DER- Optimization |  |  |  |  | line | 33
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduling electricity consumption (plug loads, white goods, etc.) | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automated management of local electricity consumption based on current renewable energy availability | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | 0 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
► | E-5 | Control of combined heat and power plant (CHP) |  | Service group: | DER - Generation Control |  |  |  |  | line | 47
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | CHP control based on scheduled runtime management and/or current heat energy demand | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | 2 | 2 | 0 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
Standard?
| code | service | 0
| E-8 | Support of (micro)grid operation modes |  | Service group: | DSM- Storage |  |  |  |  | line | 61
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automated management of (building-level) electricity consumption based on grid signals | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 2 | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | 0 | 3 | 0 | 3 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | IEC TC 57 | IEC TC 57 |  |  |  | IEC TC 57 | IEC TC 57
| code | service | 1
| E-11 | Reporting information regarding energy storage |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 76
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current state of charge (SOC) data available | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service | 1
| E-12 | Reporting information regarding electricity consumption |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 90
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | reporting on current electricity consumption on building level | 0 | 0 | 0 | 0 | 0 | 0 | 1
| level 2 | real-time feedback or benchmarking on building level | 1 | 0 | 0 | 0 | 0 | 0 | 2
| level 3 | real-time feedback or benchmarking on appliance level | 2 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | real-time feedback or benchmarking on appliance level with automated personalized recommendations | 3 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service | 0
| E-E1 | User defined smart ready service 31 |  | Service group: | User defined service group 31 |  |  |  |  | line | 106
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| E-E2 | User defined smart ready service 32 |  | Service group: | User defined service group 32 |  |  |  |  | line | 120
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| E-E3 | User defined smart ready service 33 |  | Service group: | User defined service group 33 |  |  |  |  | line | 134
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| E-E4 | User defined smart ready service 34 |  | Service group: | User defined service group 34 |  |  |  |  | line | 148
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| E-E5 | User defined smart ready service 35 |  | Service group: | User defined service group 35 |  |  |  |  | line | 162
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## EV
| Domain | Electric vehicle charging
| code | service | 1
► | EV-15 | EV Charging Capacity |  | Service group: | EV Charging |  |  |  |  | line | 4
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | not present | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | ducting (or simple power plug) available | 0 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | 0-9% of parking spaces has recharging points | 0 | 0 | 0 | 2 | 0 | 0 | 0
| level 3 | 10-50% or parking spaces has recharging point | 0 | 0 | 0 | 3 | 0 | 0 | 0
| level 4 | >50% of parking spaces has recharging point | 0 | 0 | 0 | 3 | 0 | 0 | 0
Information sources
Standard?
| code | service | 1
► | EV-16 | EV Charging Grid balancing |  | Service group: | EV Charging - Grid |  |  |  |  | line | 18
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Not present (uncontrolled charging) | 0 | -2 | 0 | 0 | 0 | 0 | 0
| level 1 | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 0 | 1 | 0 | 2 | 0 | 0 | 0
| level 2 | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 0 | 3 | 0 | 2 | 0 | 0 | 0
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
► | EV-17 | EV charging information and connectivity |  | Service group: | EV Charging - connectivity |  |  |  |  | line | 32
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No information available | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on EV charging status to occupant | 0 | 0 | 0 | 1 | 0 | 0 | 2
| level 2 | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | 0 | 1 | 0 | 1 | 0 | 0 | 3
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
| EV-E1 | User defined smart ready service 36 |  | Service group: | User defined service group 36 |  |  |  |  | line | 47
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| EV-E2 | User defined smart ready service 37 |  | Service group: | User defined service group 37 |  |  |  |  | line | 61
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| EV-E3 | User defined smart ready service 38 |  | Service group: | User defined service group 38 |  |  |  |  | line | 75
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| EV-E4 | User defined smart ready service 39 |  | Service group: | User defined service group 39 |  |  |  |  | line | 89
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| EV-E5 | User defined smart ready service 40 |  | Service group: | User defined service group 40 |  |  |  |  | line | 103
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## MC
| Domain | Monitoring and control
| code | service | 0
► | MC-3 | Run time management of HVAC systems |  | Service group: | HVAC interaction control |  |  |  |  | line | 5
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual setting | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Runtime setting of heating and cooling plants following a predefined time schedule | 1 | 1 | 1 | 1 | 0 | 0 | 0
| level 2 | Heating and cooling plant on/off control based on building loads | 2 | 1 | 2 | 2 | 1 | 0 | 0
| level 3 | Heating and cooling plant on/off control based on predictive control or grid signals | 3 | 2 | 2 | 3 | 1 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
► | MC-4 | Detecting faults of technical building systems and providing support to the diagnosis of these faults |  | Service group: | Fault detection |  |  |  |  | line | 19
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No central indication of detected faults and alarms | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | With central indication of detected faults and alarms for at least 2 relevant TBS | 0 | 0 | 0 | 1 | 1 | 1 | 1
| level 2 | With central indication of detected faults and alarms for all relevant TBS | 0 | 0 | 0 | 2 | 2 | 2 | 2
| level 3 | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | 0 | 0 | 0 | 3 | 3 | 3 | 3
| level 4 | 0
Information sources
Standard?
| code | service | 0
► | MC-9 | Occupancy detection: connected services |  | Service group: | TBS interaction control |  |  |  |  | line | 34
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Occupancy detection for individual functions, e.g. lighting | 1 | 0 | 1 | 1 | 0 | 1 | 0
| level 2 | Centralised occupant detection which feeds in to several TBS such as lighting and heating | 1 | 0 | 1 | 1 | 0 | 2 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
Standard?
| code | service | 1
► | MC-13 | Central reporting of TBS performance and energy use |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 50
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of realtime energy use per energy carrier | 1 | 0 | 0 | 1 | 0 | 1 | 1
| level 2 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | 1 | 0 | 0 | 2 | 0 | 2 | 2
| level 3 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | 1 | 0 | 0 | 3 | 0 | 3 | 3
| level 4 | 0
Information sources
Standard?
| code | service | 1
| MC-25 | Smart Grid Integration |  | Service group: | Smart Grid Integration |  |  |  |  | line | 66
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None - No harmonization between grid and TBS; building is operated independently from the grid load | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Demand side management possible for (some) individual TBS, but not coordinated over various domains | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | Coordinated demand side management of multiple TBS | 1 | 3 | 0 | 1 | 0 | 0 | 0
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
| MC-28 | Reporting information regarding demand side management performance and operation |  | Service group: | Feedback - Reporting information |  |  |  |  | line | 81
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on current DSM status, including managed energy flows | 0 | 1 | 0 | 0 | 0 | 0 | 2
| level 2 | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | 0 | 2 | 0 | 0 | 0 | 1 | 3
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
| MC-29 | Override of DSM control |  | Service group: | Override control |  |  |  |  | line | 95
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No DSM control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | DSM control without the possibility to override this control by the building user (occupant or facility manager) | 0 | 3 | -2 | 0 | 0 | -1 | -2
| level 2 | Manual override and reactivation of DSM control by the building user | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 3 | Scheduled override of DSM control (and reactivation) by the building user | 0 | 1 | 0 | 2 | 0 | 1 | 0
| level 4 | Scheduled override of DSM control and reactivation with optimised control | 0 | 2 | 0 | 3 | 0 | 1 | 0
Information sources
Standard?
| code | service | 1
| MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals |  | Service group: | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals |  |  |  |  | line | 109
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Single platform that allows manual control of multiple TBS | 0 | 0 | 0 | 1 | 0 | 1 | 0
| level 2 | Single platform that allows automated control & coordination between TBS | 1 | 0 | 0 | 2 | 0 | 1 | 0
| level 3 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 2 | 0 | 0 | 3 | 0 | 1 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 0
| MC-E1 | User defined smart ready service 41 |  | Service group: | User defined service group 41 |  |  |  |  | line | 124
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| MC-E2 | User defined smart ready service 42 |  | Service group: | User defined service group 42 |  |  |  |  | line | 138
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| MC-E3 | User defined smart ready service 43 |  | Service group: | User defined service group 43 |  |  |  |  | line | 152
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| MC-E4 | User defined smart ready service 44 |  | Service group: | User defined service group 44 |  |  |  |  | line | 166
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 0
| MC-E5 | User defined smart ready service 45 |  | Service group: | User defined service group 45 |  |  |  |  | line | 180
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | User defined level 1-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | User defined level 1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | User defined level 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | User defined level 1-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | User defined level 1-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?